## Model Element Table
|  |  |  | Use on this project |  |  | SD |  |  | DD |  |  | CD |  |  | Estimating |  |  | Estimating |  |  | LEED Cert. |  |  | LEED Cert
[16 empty] | Est. 1 |  |  | Bid Pkg. |  |  | Check |  |  | Submittal
UniFormat Level | [6 empty] | Date |  |  | Date |  |  | Date |  |  | Date |  |  | Date |  |  | Date |  |  | Date
1 | 2 | 3 | 4 |  |  | Relevant Attribute Tables | LOD | MEA | Notes | LOD | MEA | Notes | LOD | MEA | Notes | LOD | MEA | Notes | LOD | MEA | Notes | LOD | MEA | Notes | LOD | MEA | Notes
A |  |  |  |  | SUBSTRUCTURE
A | 10 |  |  |  | Foundations | A, B Concrete; A, B Wood; A, B Masonry; A, B Precast Concrete
A | 10 | 10 |  |  | Standard Foundations | A, B Concrete; A, B Wood; A, B Masonry; A, B Precast Concrete
A | 10 | 10 | 0.1 |  | Wall Foundations | A, B Concrete; A, B Wood; A, B Masonry; A, B Precast Concrete
A | 10 | 10 | 0.3 |  | Column Foundations | A, B Concrete; A, B Wood; A, B Masonry; A, B Precast Concrete
A | 10 | 20 |  |  | Special Foundations | A, B Concrete; A, B Wood; A, B Masonry; A, B Precast Concrete
A | 10 | 20 | 0.8 |  | Grade Beams | A, B Concrete; A, B Wood; A, B Masonry; A, B Precast Concrete
A | 20 |  |  |  | Subgrade Enclosures | A, B Concrete; A, B Wood; A, B Masonry; A, B Precast Concrete
A | 20 | 10 |  |  | Walls for Subgrade Enclosures | A, B Concrete; A, B Wood; A, B Masonry; A, B Precast Concrete
A | 40 |  |  |  | Slabs-on-Grade | A, B - Str. Concrete
A | 40 | 10 |  |  | Standard Slabs-on-Grade | A, B Concrete
A | 40 | 20 |  |  | Structural Slabs-on-Grade | A, B Concrete
B |  |  |  |  | SHELL
B | 10 |  |  |  | Superstructure
B | 10 | 10 |  |  | Floor Construction | A, B Cold Formed Metal Framing; A, B Masonry; A, B Metal Deck; A, B Precast Concrete; A,B Steel Joist; A, B Structural Steel; A, B Concrete; A, B Wood
B | 10 | 10 | 0.1 |  | Floor Structural Frame
B | 10 | 10 | 0.1 |  | Concrete | A, B Concrete
B | 10 | 10 | 0.1 |  | Masonry | A, B Masonry
B | 10 | 10 | 0.1 |  | Steel Framing Columns | A, B Structural Steel
B | 10 | 10 | 0.1 |  | Steel Framing Beams | A, B Structural Steel
B | 10 | 10 | 0.1 |  | Steel Framing Bracing Rods | A, B Structural Steel
B | 10 | 10 | 0.1 |  | Steel Joists | A,B Steel Joist
B | 10 | 10 | 0.1 |  | Cold-Formed Metal Framing | A, B Cold Formed Metal Framing
B | 10 | 10 | 0.1 |  | Wood Floor Trusses | A, B Wood
B | 10 | 10 | 0.2 |  | Floor Decks, Slabs, and Toppings
B | 10 | 10 | 0.2 |  | Wood Floor Deck | A, B Wood
B | 10 | 10 | 0.2 |  | Metal Floor Deck | A, B Metal Deck
B | 10 | 10 | 0.2 |  | Composite Floor Deck | A, B Structural Steel; A, B Concrete
B | 10 | 10 | 0.2 |  | Concrete | A, B Concrete
B | 10 | 20 |  |  | Roof Construction | A, B Cold Formed Metal Framing; A, B Masonry; A, B Metal Deck; A, B Precast Concrete; A,B Steel Joist; A, B Structural Steel; A, B Concrete; A, B Wood
B | 10 | 20 | 0.1 |  | Roof Structural Frame | A, B Structural Steel; A, B Concrete; A,B Steel Joist
B | 10 | 20 | 0.2 |  | Roof Decks, Slabs, and Sheathing | A,B Steel Joist; A, B Metal Deck
B | 10 | 20 | 0.3 |  | Canopy Construction
B | 10 | 80 |  |  | Stairs | A, B Cold Formed Metal Framing; A, B Masonry; A, B Metal Deck; A, B Precast Concrete; A, B Structural Steel; A, B Concrete; A, B Wood
B | 10 | 80 | 0.1 |  | Stair Construction | A, B Structural Steel; A, B Precast Concrete; A, B Concrete
B | 10 | 80 | 0.5 |  | Stair Railings | A, B Structural Steel; A, B Precast Concrete; A, B Concrete
B | 10 | 80 | 0.6 |  | Fire Escapes | A, B Structural Steel; A, B Precast Concrete; A, B Concrete
B | 10 | 80 | 0.7 |  | Metal Walkways | A, B Structural Steel; A, B Precast Concrete; A, B Concrete
B | 10 | 80 | 0.8 |  | Ladders | A, B Structural Steel
B | 20 |  |  |  | Exterior Vertical Enclosures
B | 20 | 10 |  |  | Exterior Walls | B – Ext. Wall
B | 20 | 10 | 0.1 |  | Exterior Wall Veneer | A, B Masonry
B | 20 | 10 | 0.2 |  | Exterior Wall Construction | A, B Cold Formed Metal Framing; A, B Wood
B | 20 | 10 | 0.3 |  | Exterior Wall Interior Skin
B | 20 | 10 | 0.5 |  | Parapets
B | 20 | 10 | 0.6 |  | Equipment Screens
B | 20 | 20
B | 20 | 20 |  |  | Exterior Windows | B – Ext. Openings
B | 20 | 20 | 0.1 |  | Exterior Operating Windows
B | 20 | 20 | 0.2 |  | Exterior Fixed Windows
B | 20 | 20 | 0.3 |  | Exterior Window Wall
B | 20 | 20 | 0.5 |  | Exterior Special Function Windows
B | 20 | 50 |  |  | Exterior Doors and Grilles | B – Ext. Doors
B | 20 | 50 | 0.1 |  | Exterior Entrance Doors
B | 20 | 50 | 0.2 |  | Exterior Utility Doors
B | 20 | 50 | 0.3 |  | Exterior Oversize Doors
B | 20 | 50 | 0.4 |  | Exterior Special Function Doors
B | 20 | 50 | 0.6 |  | Exterior Grilles
B | 20 | 50 | 0.7 |  | Exterior Gates
B | 20 | 50 | 0.9 |  | Exterior Door Supplementary Components
B | 20 | 70 |  |  | Exterior Louvers and Vents | B - Ext. Louvers and Vents
B | 20 | 70 | 0.1 |  | Exterior Louvers
B | 20 | 70 | 0.5 |  | Exterior Vents
B | 20 | 80 |  |  | Exterior Wall Appurtenances
B | 20 | 80 | 0.1 |  | Exterior Fixed Grilles and Screens
B | 20 | 80 | 0.3 |  | Exterior Opening Protection Devices
B | 20 | 80 | 0.5 |  | Exterior Balcony Walls and Railings
B | 20 | 80 | 0.7 |  | Exterior Fabrications
B | 20 | 80 | 0.8 |  | Bird Control Devices
B | 20 | 90 |  |  | Exterior Wall Specialties
B | 30 |  |  |  | Exterior Horizontal Enclosures
B | 30 | 10 |  |  | Roofing | B – Roof
B | 30 | 10 | 0.1 |  | Steep Slope Roofing
B | 30 | 10 | 0.5 |  | Low Slope Roofing
B | 30 | 10 | 0.7 |  | Canopy Roofing
B | 30 | 10 | 0.9 |  | Roofing Supplementary Components
B | 30 | 20 |  |  | Roof Appurtenances
B | 30 | 20 | 0.1 |  | Roof Accessories
B | 30 | 20 | 0.3 |  | Roof Specialties
B | 30 | 20 | 0.7 |  | Rainwater Management
B | 30 | 40 |  |  | Traffic Bearing Horizontal Enclosures | B – Roof
B | 30 | 40 | 0.1 |  | Traffic Bearing Coatings
B | 30 | 40 | 0.3 |  | Horizontal Waterproofing Membrane
B | 30 | 40 | 0.5 |  | Wear Surfaces
B | 30 | 40 | 0.9 |  | Horizontal Enclosure Supplementary Components
B | 30 | 60 |  |  | Horizontal Openings | B – Ext. Openings
B | 30 | 60 | 0.1 |  | Roof Windows and Skylights
B | 30 | 60 | 0.5 |  | Vents and Hatches
B | 30 | 60 | 0.9 |  | Horizontal Openings Supplementary Components
B | 30 | 80 |  |  | Overhead Exterior Enclosures | Ceilings (susp. Ceilings)
B | 30 | 80 | 0.1 |  | Exterior Ceilings
B | 30 | 80 | 0.2 |  | Exterior Soffits
B | 30 | 80 | 0.3 |  | Exterior Bulkheads
C |  |  |  |  | INTERIORS
C | 10 |  |  |  | Interior Construction
C | 10 | 10 |  |  | Partitions | C - Partitions
C | 10 | 10 | 0.1 |  | Interior Fixed Partitions | A, B Cold Formed Metal Framing; A, B Wood; A, B Masonry
C | 10 | 10 | 0.2 |  | Interior Glazed Partitions
C | 10 | 10 | 0.4 |  | Interior Demountable Partitions
C | 10 | 10 | 0.5 |  | Interior Operable Partitions
C | 10 | 10 | 0.7 |  | Interior Screens
C | 10 | 10 | 0.9 |  | Interior Partitions Supplementary Components
C | 10 | 20 |  |  | Interior Windows | C – Int. Windows
C | 10 | 20 | 0.1 |  | Interior Operating Windows
C | 10 | 20 | 0.2 |  | Interior Fixed Windows
C | 10 | 20 | 0.5 |  | Interior Special Function Windows
C | 10 | 20 | 0.9 |  | Interior Window Supplementary Components
C | 10 | 30 |  |  | Interior Doors | C – Int. Doors
C | 10 | 30 | 0.1 |  | Interior Swinging Doors
C | 10 | 30 | 0.2 |  | Interior Entrance Doors
C | 10 | 30 | 0.25 |  | Interior Sliding Doors
C | 10 | 30 | 0.3 |  | Interior Folding Doors
C | 10 | 30 | 0.4 |  | Interior Coiling Doors
C | 10 | 30 | 0.5 |  | Interior Panel Doors
C | 10 | 30 | 0.7 |  | Interior Special Function Doors
C | 10 | 30 | 0.8 |  | Interior Access Doors and Panels
C | 10 | 30 | 0.9 |  | Interior Door Supplementary Components
C | 10 | 40 |  |  | Interior Grilles and Gates | C - Int. Doors
C | 10 | 40 | 0.1 |  | Interior Grilles
C | 10 | 40 | 0.5 |  | Interior Gates
C | 10 | 60 |  |  | Raised Floor Construction | C - Raised Floor
C | 10 | 60 | 0.1 |  | Access Flooring
C | 10 | 60 | 0.3 |  | Platform/Stage Floors
C | 10 | 70 |  |  | Suspended Ceiling Construction | C - Susp. Clg.
C | 10 | 70 | 0.1 |  | Acoustical Suspended Ceilings
C | 10 | 70 | 0.2 |  | Suspended Plaster and Gypsum Board Ceilings
C | 10 | 70 | 0.5 |  | Specialty Suspended Ceilings
C | 10 | 70 | 0.7 |  | Special Function Suspended Ceilings
C | 10 | 70 | 0.9 |  | Ceiling Suspension Components
C | 10 | 90 |  |  | Interior Specialties
C | 10 | 90 | 0.1 |  | Interior Railings and Handrails | A, B Miscellaneous Steel
C | 10 | 90 | 0.15 |  | Interior Louvers
C | 10 | 90 | 0.2 |  | Information Specialties
C | 10 | 90 | 0.25 |  | Compartments and Cubicles
C | 10 | 90 | 0.3 |  | Service Walls
C | 10 | 90 | 0.35 |  | Wall and Door Protection
C | 10 | 90 | 0.4 |  | Toilet, Bath and Laundry Accessories
C | 10 | 90 | 0.45 |  | Interior Gas Lighting
C | 10 | 90 | 0.5 |  | Fireplaces and Stoves
C | 10 | 90 | 0.6 |  | Safety Specialties
C | 10 | 90 | 0.7 |  | Storage Specialties
C | 10 | 90 | 0.9 |  | Other Interior Specialties | A, B Miscellaneous Steel
C | 20 |  |  |  | Interior Finishes
C | 20 | 10 |  |  | Wall Finishes
C | 20 | 10 | 0.1 |  | Tile Wall Finish
C | 20 | 10 | 0.2 |  | Wall Paneling
C | 20 | 10 | 0.3 |  | Wall Coverings
C | 20 | 10 | 0.35 |  | Wall Carpeting
C | 20 | 10 | 0.5 |  | Stone Facing
C | 20 | 10 | 0.6 |  | Special Wall Surfacing
C | 20 | 10 | 0.7 |  | Wall Painting and Coating
C | 20 | 10 | 0.8 |  | Acoustical Wall Treatment
C | 20 | 10 | 0.9 |  | Wall Finish Supplementary Components
C | 20 | 20 |  |  | Interior Fabrications
C | 20 | 30 |  |  | Flooring
C | 20 | 40 |  |  | Stair Finishes
C | 20 | 50 |  |  | Ceiling Finishes
D |  |  |  |  | SERVICES
D | 10 |  |  |  | Conveying
D | 10 | 10 |  |  | Vertical Conveying Systems
D | 10 | 10 | 0.1 |  | Elevators
D | 10 | 10 | 0.2 |  | Lifts
D | 10 | 10 | 0.3 |  | Escalators
D | 10 | 10 | 0.5 |  | Dumbwaiters
D | 10 | 10 | 0.6 |  | Moving Ramps
D | 10 | 30 |  |  | Horizontal Conveying
D | 10 | 30 | 0.1 |  | Moving Walks
D | 10 | 30 | 0.3 |  | Turntables
D | 10 | 30 | 0.5 |  | Passenger Loading Bridges
D | 10 | 30 | 0.7 |  | People Movers
D | 10 | 50 |  |  | Material Handling
D | 10 | 50 | 0.1 |  | Cranes
D | 10 | 50 | 0.2 |  | Hoists
D | 10 | 50 | 0.3 |  | Derrecks
D | 10 | 50 | 0.4 |  | Conveyors
D | 10 | 50 | 0.5 |  | Baggage Handling Equipment
D | 10 | 50 | 0.6 |  | Chutes
D | 10 | 50 | 0.7 |  | Pneumatic Tube Systems
D | 10 | 80 |  |  | Operable Access Systems
D | 10 | 80 | 0.1 |  | Suspended Scaffolding
D | 10 | 80 | 0.2 |  | Rope Climbers
D | 10 | 80 | 0.3 |  | Elevating Platforms
D | 10 | 80 | 0.4 |  | Powered Scaffolding
D | 10 | 80 | 0.5 |  | Building Envelope Access
D | 20 |  |  |  | Plumbing | D20 - Plumbing, D- Fluid_Gas Distribution; D50 - Electrical
D | 20 | 10 |  |  | Domestic Water Distribution
D | 20 | 10 | 0.1 |  | Facility Potable-Water Storage Tanks
D | 20 | 10 | 0.2 |  | Domestic Water Equipment
D | 20 | 10 | 0.4 |  | Domestic Water Piping
D | 20 | 10 | 0.6 |  | Plumbing Fixtures
D | 20 | 10 | 0.9 |  | Domestic Water Distribution Supplementary Components
D | 20 | 20 |  |  | Sanitary Drainage
D | 20 | 20 | 0.1 |  | Sanitary Sewerage Equipment
D | 20 | 20 | 0.3 |  | Sanitary Sewerage Piping
D | 20 | 20 | 0.9 |  | Sanitary Drainage Supplementary Components
D | 20 | 30 |  |  | Building Support Plumbing Systems
D | 20 | 30 | 0.1 |  | Stormwater Drainage Equipment
D | 20 | 30 | 0.2 |  | Stormwater Drainage Piping
D | 20 | 30 | 0.3 |  | Facility Stormwater Drains
D | 20 | 30 | 0.6 |  | Gray Water Systems
D | 20 | 30 | 0.9 |  | Building Support Plumbing System Supplementary Components
D | 20 | 50 |  |  | General Service Compressed-Air
D | 20 | 60 |  |  | Process Support Plumbing Systems
D | 20 | 90 | 0.1 |  | Compressed-Air Systems
D | 20 | 90 | 0.2 |  | Vacuum Systems
D | 20 | 90 | 0.3 |  | Gas Systems
D | 20 | 90 | 0.4 |  | Chemical-Waste Systems
D | 20 | 90 | 0.5 |  | Processed Water Systems
D | 20 | 90 | 0.9 |  | Process Support Plumbing System Supplementary Components
D | 30 |  |  |  | HVAC | D20 - Plumbing; D30 - HVAC; D- Air Distribution; D40 - Fire Protection; D- Fluid_Gas Distribution; D50 - Electrical; D- Electrical Distribution
D | 30 | 10 |  |  | Facility Fuel Systems
D | 30 | 10 | 0.1 |  | Fuel Piping
D | 30 | 10 | 0.3 |  | Fuel Pumps
D | 30 | 10 | 0.5 |  | Fuel Storage Tanks
D | 30 | 20 |  |  | Heating Systems
D | 30 | 20 | 0.1 |  | Heat Generation
D | 30 | 20 | 0.3 |  | Thermal Heat Storage
D | 30 | 20 | 0.7 |  | Decentralized Heating Equipment
D | 30 | 20 | 0.9 |  | Heating System Supplementary Components
D | 30 | 30 |  |  | Cooling Systems
D | 30 | 30 | 0.1 |  | Central Cooling
D | 30 | 30 | 0.3 |  | Evaporative Air-Cooling
D | 30 | 30 | 0.4 |  | Thermal Cooling Storage
D | 30 | 30 | 0.7 |  | Decentralized Cooling
D | 30 | 30 | 0 |  | Cooling System Supplementary Components
D | 30 | 50 |  |  | Facility HVAC Distribution Systems
D | 30 | 50 | 0.1 |  | Facility Hydronic Distribution
D | 30 | 50 | 0.3 |  | Facility Steam Distribution
D | 30 | 50 | 0.5 |  | HVAC Air Distribution
D | 30 | 50 | 0.9 |  | Facility Distribution Systems Supplementary Components
D | 30 | 60 |  |  | Ventilation
D | 30 | 60 | 0.1 |  | Supply Air
D | 30 | 60 | 0.2 |  | Return Air
D | 30 | 60 | 0.3 |  | Exhaust Air
D | 30 | 60 | 0.4 |  | Outside Air
D | 30 | 60 | 0.6 |  | Air-to-Air Energy Recovery
D | 30 | 60 | 0.7 |  | HVAC Air Cleaning
D | 30 | 60 | 0.9 |  | Ventilation Supplementary Components
D | 30 | 70 |  |  | Special Purpose HVAC Systems
D | 30 | 70 | 0.1 |  | Snow Melting
D | 40 |  |  |  | Fire Protection | D40 - Fire Protection, D- Fluid_Gas Distribution; D50 - Electrical,
D | 40 | 10 |  |  | Fire Suppression
D | 40 | 10 | 0.1 |  | Water-Based Fire-Suppression
D | 40 | 10 | 0.5 |  | Fire-Extinguishing
D | 40 | 10 | 0.9 |  | Fire Suppression Supplementary Components
D | 40 | 30 |  |  | Fire Protection Specialties
D | 40 | 30 | 0.1 |  | Fire Protection Cabinets
D | 40 | 30 | 0.3 |  | Fire Extinguishers
D | 40 | 30 | 0.5 |  | Breathing Air Replenishment Systems
D | 40 | 30 | 0.7 |  | Fire Extinguisher Accessories
D | 50 |  |  |  | Electrical | D50 - Electrical, D- Electrical Distribution
D | 50 | 10 |  |  | Facility Power Generation
D | 50 | 10 | 0.1 |  | Packaged Generator Assemblies
D | 50 | 10 | 0.2 |  | Battery Equipment
D | 50 | 10 | 0.3 |  | Photovoltaic Collectors
D | 50 | 10 | 0.4 |  | Fuel Cells
D | 50 | 10 | 0.7 |  | Transfer Switches
D | 50 | 20 |  |  | Electrical Service and Distribution
D | 50 | 20 | 0.1 |  | Electrical Service Entrance
D | 50 | 20 | 0.3 |  | Power Distribution
D | 50 | 20 | 0.7 |  | Facility Grounding
D | 50 | 30 |  |  | General Purpose Electrical Power
D | 50 | 30 | 0.1 |  | Branch Wiring System
D | 50 | 30 | 0.5 |  | Wiring Devices
D | 50 | 40 |  |  | Lighting
D | 50 | 40 | 0.1 |  | Lighting Control
D | 50 | 40 | 0.2 |  | Branch Wiring for Lighting
D | 50 | 40 | 0.5 |  | Lighting Fixtures
D | 50 | 80 |  |  | Miscellaneous Electrical Systems
D | 50 | 80 | 0.1 |  | Lightning Protection
D | 50 | 80 | 0.7 |  | Transient Voltage Suppression
D | 60 |  |  |  | Communications | D50 - Electrical, D- Electrical Distribution
D | 60 | 10 |  |  | Data Communications
D | 60 | 20 |  |  | Voice Communications
D | 60 | 30 |  |  | Audio-Video Communication
D | 60 | 60 |  |  | Distributed Communications and Monitoring
D | 60 | 90 |  |  | Communications Supplementary Components
D | 70 |  |  |  | Electronic Safety and Security | D50 - Electrical, D- Electrical Distribution
D | 70 | 10 |  |  | Access Control and Intrusion Detection
D | 70 | 30 |  |  | Electronic Surveillance
D | 70 | 50 |  |  | Detection and Alarm
D | 70 | 70 |  |  | Electronic Monitoring and Control
D | 70 | 90 |  |  | Electronic Safety and Security Supplementary Components
D | 80 |  |  |  | Integrated Automation | D50 - Electrical, D- Electrical Distribution
D | 80 | 10 |  |  | Integrated Automation Facility Controls
E |  |  |  |  | EQUIPMENT & FURNISHINGS
E | 10 |  |  |  | Equipment
E | 10 | 10 |  |  | Vehicle and Pedestrian Equipment
E | 10 | 10 | 0.1 |  | Vehicle Servicing Equipment
E | 10 | 10 | 0.3 |  | Interior Parking Control Equipment
E | 10 | 10 | 0.5 |  | Loading Dock Equipment
E | 10 | 10 | 0.7 |  | Interior Pedestrian Control Equipment
E | 10 | 30 |  |  | Commercial Equipment
E | 10 | 30 | 0.1 |  | Mercantile and Service Equipment
E | 10 | 30 | 0.2 |  | Vault Equipment
E | 10 | 30 | 0.25 |  | Teller and Service Equipment
E | 10 | 30 | 0.3 |  | Refrigerated Display Equipment
E | 10 | 30 | 0.35 |  | Commercial Laundry and Dry Cleaning Equipment
E | 10 | 30 | 0.4 |  | Maintenance Equipment
E | 10 | 30 | 0.5 |  | Hospitality Equipment
E | 10 | 30 | 0.55 |  | Unit Kitchens
E | 10 | 30 | 0.6 |  | Photographic Processing Equipment
E | 10 | 30 | 0.7 |  | Postal, Packaging and Shipping Equipment
E | 10 | 30 | 0.75 |  | Office Equipment
E | 10 | 30 | 0.8 |  | Foodservice Equipment
E | 10 | 40 |  |  | Institutional Equipment
E | 10 | 40 | 0.1 |  | Educational and Scientific Equipment
E | 10 | 40 | 0.2 |  | Healthcare Equipment
E | 10 | 40 | 0.4 |  | Religious Equipment
E | 10 | 40 | 0.6 |  | Security Equipment
E | 10 | 40 | 0.7 |  | Detention Equipment
E | 10 | 60 |  |  | Residential Equipment
E | 10 | 60 | 0.1 |  | Residential Appliances
E | 10 | 60 | 0.5 |  | Residential Stairs
E | 10 | 60 | 0.7 |  | Residential Ceiling Fans
E | 10 | 70 |  |  | Entertainment and Recreational Equipment
E | 10 | 70 | 0.1 |  | Theater and Stage Equipment
E | 10 | 70 | 0.2 |  | Musical Equipment
E | 10 | 70 | 0.5 |  | Athletic Equipment
E | 10 | 70 | 0.6 |  | Recreational Equipment
E | 10 | 90 |  |  | Other Equipment
E | 10 | 90 | 0.1 |  | Solid Waste Handling Equipment
E | 10 | 90 | 0.3 |  | Agricultural Equipment
E | 10 | 90 | 0.4 |  | Horticultural Equipment
E | 10 | 90 | 0.6 |  | Decontamination Equipment
E | 20 |  |  |  | Furnishings
E | 20 | 10 |  |  | Fixed Furnishings
E | 20 | 10 | 0.1 |  | Fixed Art
E | 20 | 10 | 0.2 |  | Window Treatments
E | 20 | 10 | 0.3 |  | Casework
E | 20 | 10 | 0.7 |  | Fixed Multiple Seating
E | 20 | 10 | 0.9 |  | Other Fixed Furnishings
E | 20 | 50 |  |  | Movable Furnishings
E | 20 | 50 | 0.1 |  | Movable Art
E | 20 | 50 | 0.3 |  | Furniture
E | 20 | 50 | 0.4 |  | Accessories
E | 20 | 50 | 0.6 |  | Movable Multiple Seating
E | 20 | 50 | 0.9 |  | Other Movable Furnishings
F |  |  |  |  | SPECIAL CONSTRUCTION & DEMOLITION
F | 10 |  |  |  | Special Construction
F | 10 | 10 |  |  | Integrated Construction
F | 10 | 20 |  |  | Special Structures
F | 10 | 30 |  |  | Special Function Construction
F | 10 | 50 |  |  | Special Facility Components
F | 10 | 60 |  |  | Athletic and Recreational Special Construction
F | 10 | 80 |  |  | Special Instrumentation
F | 20 |  |  |  | Facility Remediation
F | 20 | 10 |  |  | Hazardous Materials Remediation
F | 30 |  |  |  | Demolition
F | 30 | 10 |  |  | Structure Demolition
F | 30 | 30 |  |  | Selective Demolition
F | 30 | 50 |  |  | Structure Moving
G |  |  |  |  | BUILDING SITEWORK
G | 10 |  |  |  | Site Preparation
G | 10 | 10 |  |  | Site Clearing
G | 10 | 20 |  |  | Site Elements Demolition
G | 10 | 30 |  |  | Site Element Relocations
G | 10 | 50 |  |  | Site Remediation
G | 10 | 70 |  |  | Site Earthwork
G | 10 | 70 | 0.1 |  | Grading
G | 20 |  |  |  | Site Improvements
G | 20 | 10 |  |  | Roadways
G | 20 | 20 |  |  | Parking Lots
G | 20 | 20 | 0.1 |  | Parking Lot Pavement
G | 20 | 20 | 0.2 |  | Parking Lot Curbs and Gutters
G | 20 | 20 | 0.4 |  | Parking Lot Appurtenances
G | 20 | 30 |  |  | Pedestrian Plazas and Walkways
G | 20 | 40 |  |  | Airfields
G | 20 | 50 |  |  | Athletic, Recreational, and Playfield Areas
G | 20 | 60 |  |  | Site Development
G | 20 | 80 |  |  | Landscaping
G | 30 |  |  |  | Liquid and Gas Site Utilities
G | 30 | 10 |  |  | Water Utilities
G | 30 | 10 | 0.1 |  | Site Domestic Water Distribution
G | 30 | 10 | 0.3 |  | Site Fire Protection Water Distribution
G | 30 | 20 |  |  | Sanitary Sewerage Utilities
G | 30 | 20 | 0.2 |  | Sanitary Sewerage Piping
G | 30 | 20 | 0.5 |  | Sanitary Sewerage Structures
G | 30 | 30 |  |  | Storm Drainage Utilities
G | 30 | 50 |  |  | Site Energy Distribution
G | 30 | 60 |  |  | Site Fuel Distribution
G | 30 | 90 |  |  | Liquid and Gas Site Utilities Supplementary Components
G | 40 |  |  |  | Electrical Site Improvements
G | 40 | 10 |  |  | Site Electric Distribution Systems
G | 40 | 50 |  |  | Site Lighting
G | 50 |  |  |  | Site Communications
G | 50 | 10 |  |  | Site Communications Systems
G | 90 |  |  |  | Miscellaneous Site Construction
G | 90 | 10 |  |  | Tunnels

## A, B Structural Steel
A, B - Structural Steel
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
AISC Shape Type & Size | String | Text | options: [specific “HSS 6x6x1/4”] |  |  |  | x | x | x
Fireproofed | bool | True / False |  |  |  |  | x | x | x
Weight in pounds/foot | Decimal
ASTM Material Grade | String | Text | options: [A992, etc] |  |  |  |  | x | x
Coating | String | Text | options: [galvanized, painted for exterior exposure, etc]
Archtectural Exposed Structural Steel | bool | True / False | options: [yes, no]
Fabrication Sequence Number | Interger | Number |  | SequenceNumber |  |  |  | x | x
Shop Submital Parameters |  |  |  | {}
Date - Issued For Construction | Date Time |  |  | {DateIFC}
Date - Permited | Date Time |  |  | {DatePermitted}
Date - recieved for Shop Detailing | Date Time |  |  | {DateRecievedForShopDet}
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | {DateOutForAproval}
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | {DateFinalForFab}
Date - Fabrication Start | Date Time |  |  | {DateFabStart}
Date - Fabrication End | Date Time |  |  | {DateFabEnd}
Date - Fabrication Shipped | Date Time |  |  | {DateFabShip}
Date - Fabrication Received | Date Time |  |  | {DateFabRecieved}
Date - Erection | Date Time |  |  | {DateErected}
Date - Inspected | Date Time |  |  | {DateInspected}

## A, B Miscellaneous Steel
A, B Miscellaneous Steel
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
AISC Shape & Size | String | Text | [5 empty] | x | x
Fireproofed | bool | True / False | [5 empty] | x | x
Weight in pounds/foot | Decimal
ASTM Material Grade | String | Text | options: [A992, etc] |  |  |  |  | x | x
Coating | String | Text | options: [galvanized, painted for exterior exposure, etc]
Archtectural Exposed Structural Steel | bool | True / False | options: [yes, no]
Fabrication Sequence Number | Interger | Number |  | SequenceNumber |  |  |  | x | x
Shop Submital Parameters |  |  |  | {}
Date - Issued For Construction | Date Time |  |  | {DateIFC}
Date - Permited | Date Time |  |  | {DatePermitted}
Date - recieved for Shop Detailing | Date Time |  |  | {DateRecievedForShopDet}
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | {DateOutForAproval}
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | {DateFinalForFab}
Date - Fabrication Start | Date Time |  |  | {DateFabStart}
Date - Fabrication End | Date Time |  |  | {DateFabEnd}
Date - Fabrication Shipped | Date Time |  |  | {DateFabShip}
Date - Fabrication Received | Date Time |  |  | {DateFabRecieved}
Date - Erection | Date Time |  |  | {DateErected}
Date - Inspected | Date Time |  |  | {DateInspected}

## A, B Concrete
A, B - Concrete
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Member Type | Integer |  | (0) Foundation (1) Beam (2) Column (3) Slab (4) Wall |  |  | x | x | x | x
Concrete Compression Strength |  | PSI |  | Example: 3000 PSI |  |  | x | x | x
Reinforcing Steel Flexture |  | PSI |  | Example: 60,000 PSI |  |  | x | x | x
Reinforcing Steel Shear |  | PSI |  | Example: 60,000 PSI |  |  | x | x | x
Exterior Exposure | Bool | True \ False
Shop Submital Parameters
Date - Issued For Construction | Date Time |  |  | DateIFC
Date - Permited | Date Time |  |  | DatePermitted
Date - recieved for Shop Detailing | Date Time |  |  | DateRecievedForShopDet
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | DateOutForAproval
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | DateFinalForFab
Date - Fabrication Start | Date Time |  |  | DateFabStart
Date - Fabrication End | Date Time |  |  | DateFabEnd
Date - Fabrication Shipped | Date Time |  |  | DateFabShip
Date - Fabrication Received | Date Time |  |  | DateFabRecieved
Date - Erection | Date Time |  |  | DateErected
Date - Inspected | Date Time |  |  | DateInspected

## A, B Steel Joist
A, B - Steel Open Web Joists
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Type | String | Text | K, LH, DLH, Joist Girder | {JoistType} |  | x | x | x | x
SJI Joist Designation | String | Text | options: [specific “18K3”] | {JoistDesignation} |  |  | x | x | x
Overall Length | Decimal | FT |  | {OAL} |  |  | x | x | x
Joist Depth | Decimal | in |  | {JoistDepth} |  |  | x | x | x
Approx. Wt (lbs./ft.) | Decimal | #/ft |  | {JoistApproxWt}
LRFD Load Total Safe | Decimal | Pounds / Lineal Foot |  | {Total_Load_LRFD_Safe} safe factored uniformly distributed load-carrying capacities
LRFD Load Deflection 1/360 | Decimal | Pounds / Lineal Foot |  | {Total_Load_LRFD_360} unfactored uniform load, which will produce an approximate joist deflection of 1/360 of the span
ASD Load Total Safe | Decimal | Pounds / Lineal Foot |  | {Total_Load_ASD_Safe}
ASD Load Deflection 1/360 | Decimal | Pounds / Lineal Foot |  | {Total_Load_ASD_360}
Fireproofed | bool | True / False |  | {JoistFireproofed}
Archtectural Exposed Structural Steel | bool | True / False | options: [yes, no] | {JoistAESS}
Fabrication Sequence Number | Interger | Number |  | {JoistFabSequ} SequenceNumber
Span, Base Length | Decimal | FT |  | {SpanBase}
Design Span |  |  |  | {SpanDesign}
Approximate Camber Based on Top Chord Length |  |  |  | {Camber}
Extentions (Y/N) |  |  |  | {}
Top Chord Extentions Left (Start End) | bool | True / False |  | {TCXL}
Top Chord Extentions Right (Stop End) | bool | True / False |  | {TCXR}
Bottom Chord Extension Left | bool | True / False |  | {BCXL}
Bottom Chord Extension Right | bool | True / False |  | {BCXR}
Lengths |  |  |  | {}
Bottom Chord Extension Left Length | Decimal | in |  | {BCXLL}
Bottom Chord Extension Right Length | Decimal | in |  | {BCXRL}
Top Chord Extentions Left Length | Decimal | in |  | {TCXLL}
Top Chord Extentions Right | Decimal | in |  | {TCXRL}
Recycle Content | Decimal |  | % | {RecycleContent}
Distance From Piont of Fabrication to Site | Decimal |  | Miles | {FabDistToSite}
Shop Submital Parameters |  |  |  | {}
Date - Issued For Construction | Date Time |  |  | {DateIFC}
Date - Permited | Date Time |  |  | {DatePermitted}
Date - recieved for Shop Detailing | Date Time |  |  | {DateRecievedForShopDet}
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | {DateOutForAproval}
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | {DateFinalForFab}
Date - Fabrication Start | Date Time |  |  | {DateFabStart}
Date - Fabrication End | Date Time |  |  | {DateFabEnd}
Date - Fabrication Shipped | Date Time |  |  | {DateFabShip}
Date - Fabrication Received | Date Time |  |  | {DateFabRecieved}
Date - Erection | Date Time |  |  | {DateErected}
Date - Inspected | Date Time |  |  | {DateInspected}
Engineering Parameters |  |  |  | {}
Joist Moment Of Inertia |  | in^4 |  | {Ij}
Section Modulous |  | in^3 |  | {Sx}
Slope "X" Low End ("X": 12") | Decimal | in |  | {SlopeXLow}
Slope "X" High End ("X": 12") | Decimal | in |  | {SlopeXHigh}
Bearing Depth Left | Decimal | in |  | {BearingDepthLeft}
Bearing Depth Right | Decimal | in |  | {BearingDepthRight}
Approximate Duct Opening Size Round | Decimal | in |  | {}
Approximate Duct Opening Size Square | Decimal | in |  | {}
Approximate Duct Opening Size Rectangular (Width x Highth) | Decimal | in |  | {}
Approximate Duct Opening Size Rectangular (Width x Highth) |  |  |  | {}
Chord Yield Strength | decimal |  |  | {FyChord} Refer to SJI Specifiation.
All Other Yield Strength | decimal |  |  | {FyOther} Refer to current SJI Specification
Number Of Rows Of Top Chord Bridging (Estimated per SJI Table) | Interger |  |  | {TopChordBrdRowReqEst}
Bearing Seat Attachment Left (start end) |  |  |  | {BearingTypeLeft} Bearing Seat Attachemnt Type: (1) Masonry or Concrete (2) Steel (3) Other
Bearing Seat Attachment Right (stop end) |  |  |  | {BearingTypeRight} Bearing Seat Attachemnt Type: (1) Masonry or Concrete (2) Steel (3) Other
Bearing Seat Uplift Left |  |  |  | {BrUpliftLeft} Is the joist seat in uplift
Bearing Seat Uplift Right |  |  |  | {BrUpliftRight} Is the joist seat in uplift
Laterally Unbraced Top Chords (Y/N) |  | y/n |  | {LatUnbacedTopChord}
Wood Nailers on Top Chored (Y/N) |  | y/n |  | {WoodNailers}
{}
LRFD Load Total Safe |  | Pounds / Lineal Foot |  | {} safe factored uniformly distributed load-carrying capacities
LRFD Load Deflection 1/360 |  | Pounds / Lineal Foot |  | {} unfactored uniform load, which will produce an approximate joist deflection of 1/360 of the span
ASD Load Total Safe |  | Pounds / Lineal Foot |  | {}
ASD Load Deflection 1/360 |  | Pounds / Lineal Foot |  | {}
{}
Top Chord Extention Type (None, S or R) Left | Integer |  |  | {TCExTypeLeft} Top Chord Extention Type: (0) None (1) "S", top angles of top chord (2) top and bottom angle of top chord
Top Chord Extention Type (None, S or R) Right | Integer |  |  | {TCExTypeRight} Top Chord Extention Type: (0) None (1) "S", top angles of top chord (2) top and bottom angle of top chord

## A, B Precast Concrete
A, B - Precast Concrete
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Member Type | Integer |  | (0) Foundation (1) Beam (2) Column (3) Slab (4) Wall |  |  | x | x | x | x
Concrete Compression Strength |  | PSI |  | Example: 3000 PSI |  |  | x | x | x
Reinforcing Steel Flexture |  | PSI |  | Example: 60,000 PSI |  |  | x | x | x
Reinforcing Steel Shear |  | PSI |  | Example: 60,000 PSI |  |  | x | x | x
Member Casting Number
Exterior Exposure | Bool | True \ False
Shop Submital Parameters
Date - Issued For Construction | Date Time |  |  | DateIFC
Date - Permited | Date Time |  |  | DatePermitted
Date - recieved for Shop Detailing | Date Time |  |  | DateRecievedForShopDet
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | DateOutForAproval
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | DateFinalForFab
Date - Fabrication Start | Date Time |  |  | DateFabStart
Date - Fabrication End | Date Time |  |  | DateFabEnd
Date - Fabrication Shipped | Date Time |  |  | DateFabShip
Date - Fabrication Received | Date Time |  |  | DateFabRecieved
Date - Erection | Date Time |  |  | DateErected
Date - Inspected | Date Time |  |  | DateInspected

## A, B Metal Deck
A, B - Metal Deck
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Deck Type | Integer |  |  |  |  | x | x | x | x
Yield Strength (Fy) |  | PSI |  |  |  |  | x | x | x
Deck Thickness | decimal | in |  | Example 1.5"
Deck Flute Width | decimal | in |  | Example 1.5"
Shop Submital Parameters
Date - Issued For Construction | Date Time |  |  | DateIFC
Date - Permited | Date Time |  |  | DatePermitted
Date - recieved for Shop Detailing | Date Time |  |  | DateRecievedForShopDet
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | DateOutForAproval
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | DateFinalForFab
Date - Fabrication Start | Date Time |  |  | DateFabStart
Date - Fabrication End | Date Time |  |  | DateFabEnd
Date - Fabrication Shipped | Date Time |  |  | DateFabShip
Date - Fabrication Received | Date Time |  |  | DateFabRecieved
Date - Erection | Date Time |  |  | DateErected
Date - Inspected | Date Time |  |  | DateInspected

## A, B Cold Formed Metal Framing
A, B Cold Formed Metal Framing
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Member Type | Integer |  | (0) Foundation (1) Beam (2) Column (3) Slab (4) Wall |  |  | x | x | x | x
Concrete Compression Strength |  | PSI |  | Example: 3000 PSI |  |  | x | x | x
Reinforcing Steel Flexture |  | PSI |  | Example: 60,000 PSI |  |  | x | x | x
Reinforcing Steel Shear |  | PSI |  | Example: 60,000 PSI |  |  | x | x | x
Exterior Exposure | Bool | True \ False
Shop Submital Parameters
Date - Issued For Construction | Date Time |  |  | DateIFC
Date - Permited | Date Time |  |  | DatePermitted
Date - recieved for Shop Detailing | Date Time |  |  | DateRecievedForShopDet
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | DateOutForAproval
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | DateFinalForFab
Date - Fabrication Start | Date Time |  |  | DateFabStart
Date - Fabrication End | Date Time |  |  | DateFabEnd
Date - Fabrication Shipped | Date Time |  |  | DateFabShip
Date - Fabrication Received | Date Time |  |  | DateFabRecieved
Date - Erection | Date Time |  |  | DateErected
Date - Inspected | Date Time |  |  | DateInspected

## A, B Wood
A, B - Wood
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Member Type | Integer |  | (0) Foundation (1) Beam (2) Column (3) Deck (4) Wall |  |  | x | x | x | x
Flextural Strength (Fb) |  | PSI |  |  |  |  | x | x | x
Shear Strength (Fv) |  | PSI |  |  |  |  | x | x | x
Wet Use | bool | True \ False
Repetiive Member Use | bool | True \ False
Shop Submital Parameters
Date - Issued For Construction | Date Time |  |  | DateIFC
Date - Permited | Date Time |  |  | DatePermitted
Date - recieved for Shop Detailing | Date Time |  |  | DateRecievedForShopDet
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | DateOutForAproval
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | DateFinalForFab
Date - Fabrication Start | Date Time |  |  | DateFabStart
Date - Fabrication End | Date Time |  |  | DateFabEnd
Date - Fabrication Shipped | Date Time |  |  | DateFabShip
Date - Fabrication Received | Date Time |  |  | DateFabRecieved
Date - Erection | Date Time |  |  | DateErected
Date - Inspected | Date Time |  |  | DateInspected

## A, B Masonry
A, B - Masonry
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Wall Type | [5 empty] | x | x | x | x
Wall Total Thickness |  |  | 7 5/8" |  |  |  | x | x | x
Wall Core Masonry Thickness |  |  | 7 5/8" |  |  |  | x | x | x
Wall Finish Face 1 |  |  | 3 5/8" |  |  |  | x | x | x
Wall Finish Face 2 | [6 empty] | x | x | x
Wall Is Load Bearing | Bool | Yes / No |  | IsLoadBearning |  | x | x | x | x
Block Type |  |  | CMUx8x8x16 |  |  |  |  | x | x
Shop Submital Parameters
Date - Issued For Construction | Date Time |  |  | DateIFC
Date - Permited | Date Time |  |  | DatePermitted
Date - recieved for Shop Detailing | Date Time |  |  | DateRecievedForShopDet
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | DateOutForAproval
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | DateFinalForFab
Date - Fabrication Start | Date Time |  |  | DateFabStart
Date - Fabrication End | Date Time |  |  | DateFabEnd
Date - Fabrication Shipped | Date Time |  |  | DateFabShip
Date - Fabrication Received | Date Time |  |  | DateFabRecieved
Date - Erection | Date Time |  |  | DateErected
Date - Inspected | Date Time |  |  | DateInspected

## B - Ext. Louvers and Vents
B - Ext. Louvers and Vents
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Material | Text |  | options:[Aluminium Framed, Bronze Framed, Stainless Steel Framed, Channel Glass] |  |  |  | x | x | x
Type | Text |  | Intake, Exhaust |  |  |  | x | x | x
Windbourne Debris Resistance | Numeric | psf
Wind Load Capacity |  | psf
Adjustable | Logical
Air Flow | Numeric | cfm | options:[yes, no, class]
Forced Entry Resistance | Logical |  | options:[yes, no, class]

## B – Ext. Glazed Openings
B – Ext. Glazed Openings
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Construction | Text |  | options:[Unitized (combined glass and frame), Stick Built, Structural Glass] |  |  | x | x | x | x
Material | Text |  | options:[Aluminium Framed, Bronze Framed, Stainless Steel Framed, Channel Glass] |  |  |  | x | x | x
Thermal Resistance | Number | R-Value |  |  |  |  | x | x | x
Condensation Resistance |  |  | options:[yes, no, class]
Windbourne Debris Resistance |  | psf
Wind Load Capacity |  | psf
Glazing Method |  |  | options:[Conventional, Two Sided, Three Sided, Four Sided, Pint Supported]
Glass - Material |  |  | options:[Glass, Plastic]
Glass - Configuration |  |  | options:[Monolithic, Insulating]
Glass - Condition |  |  | options, multiple:[Annealed, Heat Strengthend, Tempered, Laminated, Bent]
Glass - Coatings |  |  | options, multiple:[Purolytic (hard coat), Sputter (soft coat), Low E, Metallic, Ceramic Frit, Opaci Coat, Digital Printed]
Glass - Use |  |  | options, multiple:[Glazing into conventional application, Glazing into structurally glazed application, Mirror, Decorative, Fire Resistant, Huricane Resistant, Cable Suspended, Switchable Glass, Elecrronically Controlled switchable Glass, Pressure Resistant, Radiation Resistant, Security, Ballistics Resistant]
Water Resistance |  |  | options:[yes, no, class]
Air Infiltration |  |  | options:[yes, no, class]
Shading Coefficient |  |  | options:[yes, no, class]
Solar Heat Gain |  |  | options:[yes, no, class]
Visible Light Transmission |  |  | options:[yes, no, class]
Sound Transmission |  |  | options:[yes, no, class]
Forced Entry Resistance |  |  | options:[yes, no, class]
Bullet Resistance |  |  | options:[yes, no, class]
Radio Frequency Interference Protection |  |  | options:[yes, no, class]
Radiation Protection |  |  | options:[yes, no, class]

## B – Ext. Doors
B – Ext. Doors
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Example Project-Specific Milestones
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Type | Text | N/A | single, double, sliding, etc. |  |  | x | x | x | x
Material - frame | Text | N/A | wood, metal, glass, etc. |  |  |  | x | x | x
Material - panel | Text | N/A | solid core / hollow core, wood/metal, etc. |  |  |  | x | x | x
Hardware set | Text | N/A | reference to schedule |  |  |  | x | x | x
Fire Rating | Text | N/A | options: [UL label - A,B,C,D,E,S] |  |  |  | x | x | x
Coating - frame |  |  | options, multiple:[Purolytic (hard coat), Sputter (soft coat), Low E, Metallic, Ceramic Frit, Opaci Coat, Digital Printed]
Coating - panel
Wind Load Capacity |  |  | psf
Windbourne Debris Resistance |  |  | options:[yes, no, class]
Thermal Resistance |  |  | R-value (h·ft2·°F/Btu)
Air Infiltration |  |  | options:[yes, no, class]
Shading Coefficient |  |  | options:[yes, no, class]
Solar Heat Gain |  |  | options:[yes, no, class]
Visible Light Transmission |  |  | options:[yes, no, class]
Sound Transmission |  |  | options:[yes, no, class]
Forced Entry Resistance |  |  | options:[yes, no, class]
Bullet Resistance |  |  | options:[yes, no, class]
Radio Frequency Interference Protection |  |  | options:[yes, no, class]
Radiation Protection |  |  | options:[yes, no, class]
Egress Category |  |  | options: [UL label - "none" or "panic hardware"

## B – Cladding
B – Cladding
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Construction | Text | N/A | options:[Unitized (combined glass and frame, Stick Built, Structural Glass] |  |  |  | x | x | x
Material | Text | N/A | options:[Aluminium Framed, Bronze Framed, Stainless Steel Framed, Channel Glass] |  |  |  | x | x | x
Coatings | Text | N/A | options, multiple:[Purolytic (hard coat), Sputter (soft coat), Low E, Metallic, Ceramic Frit, Opaci Coat, Digital Printed] |  |  |  | x | x | x
Wind Load Capacity (pressure) |  |  | psf
Wind Load Capacity (drag) |  |  | psf
Windbourne Debris Resistance |  |  | options:[yes, no, class]
Thermal Resistance |  |  | R-value (h·ft2·°F/Btu)
Condensation Resistance |  |  | options:[yes, no, class]
Water Resistance |  |  | options:[yes, no, class]
Air Infiltration |  |  | options:[yes, no, class]
Sound Transmission |  |  | options:[yes, no, class]
Bullet Resistance |  |  | options:[yes, no, class]
Radiation Protection |  |  | options:[yes, no, class]
Fire Rating |  |  | options: [UL label - A,B,C,D,E,S]

## B – Roof
B – Roof
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Material - skin | Text |  | tiles, composite, sheet metal, etc. |  |  |  | x | x | x
Material - substrate | Text |  | corrugated metal, plywood, composite panels, etc. |  |  |  | x | x | x
Material - insulation | Text |  | Batt, rigid, etc. |  |  |  | x | x | x
Thermal Resistance | Number | R-value |  |  |  |  | x | x | x
Coatings (if applicable)
Wind Load Capacity (pressure) |  |  | psf
Wind Load Capacity (drag) |  |  | psf
Windbourne Debris Resistance |  |  | options:[yes, no, class]
Condensation Resistance |  |  | options:[yes, no, class]
Water Resistance |  |  | options:[yes, no, class]
Air Infiltration |  |  | options:[yes, no, class]
Radio Frequency Interference Protection |  |  | options:[yes, no, class]
Radiation Protection |  |  | options:[yes, no, class]
Fire Rating |  |  | options: [UL label - A,B,C,D,E,S]
Impact resistance (hail)
UV Resistance

## B – Ext. Wall
B – Ext. Wall
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Construction | Text | N/A | framed, unit masonry, panelized, EFIS, etc. |  |  |  | x | x | x
Material - skin | Text | N/A | tiles, composite, sheet metal, etc. |  |  |  | x | x | x
Material - substrate | Text | N/A | corrugated metal, plywood, composite panels, etc. |  |  |  | x | x | x
Material - insulation
Coatings (if applicable)
Wind Load Capacity (pressure) |  |  | psf
Wind Load Capacity (drag) |  |  | psf
Thermal Resistance |  |  | R-value (h·ft2·°F/Btu)
Condensation Resistance |  |  | options:[yes, no, class]
Water Resistance |  |  | options:[yes, no, class]
Air Infiltration |  |  | options:[yes, no, class]
Fire Rating |  |  | options: [UL label - A,B,C,D,E,S]
Impact resistance (hail) |  |  | options:[yes, no, class]
UV Resistance |  |  | options:[yes, no, class]

## C - Int. Windows
C - Int. Windows
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Construction | Text |  | options:[Unitized (combined glass and frame), Stick Built, Structural Glass] |  |  | x | x | x | x
Material | Text |  | options:[Aluminium Framed, Bronze Framed, Stainless Steel Framed, Channel Glass] |  |  |  | x | x | x
Thermal Resistance | Number | R-Value |  |  |  |  | x | x | x
Wind Load Capacity |  |  | psf
Glazing Method |  |  | options:[Conventional, Two Sided, Three Sided, Four Sided, Pint Supported]
Glass - Material |  |  | options:[Glass, Plastic]
Glass - Configuration |  |  | options:[Monolithic, Insulating]
Glass - Condition |  |  | options, multiple:[Annealed, Heat Strengthend, Tempered, Laminated, Bent]
Glass - Coatings |  |  | options, multiple:[Purolytic (hard coat), Sputter (soft coat), Low E, Metallic, Ceramic Frit, Opaci Coat, Digital Printed]
Glass - Use |  |  | options, multiple:[Glazing into conventional application, Glazing into structurally glazed application, Mirror, Decorative, Fire Resistant, Huricane Resistant, Cable Suspended, Switchable Glass, Elecrronically Controlled switchable Glass, Pressure Resistant, Radiation Resistant, Security, Ballistics Resistant]
Visible Light Transmission |  |  | options:[yes, no, class]
Sound Transmission |  |  | options:[yes, no, class]
Forced Entry Resistance |  |  | options:[yes, no, class]
Bullet Resistance |  |  | options:[yes, no, class]
Radio Frequency Interference Protection |  |  | options:[yes, no, class]
Radiation Protection |  |  | options:[yes, no, class]

## C - Int. Doors
C - Int. Doors
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Type | Text | N/A | single, double, sliding, etc. |  |  | x | x | x | x
Material - frame | Text | N/A | wood, metal, glass, etc. |  |  |  | x | x | x
Material - panel | Text | N/A | solid core / hollow core, wood/metal, etc. |  |  |  | x | x | x
Hardware set | Text | N/A | reference to schedule |  |  |  | x | x | x
Fire Rating | Text | N/A | options: [UL label - A,B,C,D,E,S] |  |  |  | x | x | x
Level |  |  | options:[First Floor, Second Floor, etc.]
Sill Height |  |  | options:[dimension: 0, 1'-0", etc.]
Frame Setback |  |  | options:[dimension: 1", 2", etc]
Frame Type |  |  | options:[reference to schedule]
Glazing Type |  |  | options:[reference to schedule]
Jamb Detail |  |  | options:[reference to schedule]
Head Detail |  |  | options:[reference to schedule]
Comments |  |  | options:[reference to schedule]
Mark |  |  | options:[reference to schedule]
Phase Created |  |  | options:[Existing, New Construction, Phase 1, Phase 2, etc.]
Head Height |  |  | options:[dimension: 7'-0", etc.]
Undercut |  |  | options:[yes, no]
Function |  |  | options:[Interior, Exterior]
Panel Thickness |  |  | options:[1 3/4", 2", etc.]
Rought Width |  |  | options:[3'-4", 3'-10", etc.]
Rought Height |  |  | options:[7'-2", etc.]
Jamb Size |  |  | options:[dimension: 1 3/4", 2", etc.]
Head Size |  |  | options:[dimension: 1 3/4", 2", 4", etc.]
Height |  |  | options:[7'-0", etc.]
Width |  |  | options:[3'-0", 3'-6", etc.]
Smoke Rated |  |  | options:[yes, no]
Model |  |  | options:[manufacturer specific information]
Manufacturer |  |  | options:[manufacturer specific information]
Glazing Material |  |  | options:[Tempered, Laminted, Decorative, etc.]
Automated Control |  |  | options:[yes, no]
Phase Demolished |  |  | options:[New Construction, Phase 1, Phase 2, etc.]
Egress Door |  |  | options:[yes, no]
Egress Capcity |  |  | options:[144, 240, etc.]
Stile Type |  |  | options:[Wide, Medium, Narrow, etc.]
Sidelite Glass Thickness |  |  | options:[dimension: 1/4", etc.]
Sidelite Glass Width |  |  | options:[dimension: 3'-0", 3'-8", etc.]
Number of Sidelites |  |  | options:[1, 2, 3, etc.]
Double Acting |  |  | options:[yes, no]
Louver Material |  |  | options:[Steel, Aluminum, etc.]
Glazing Width |  |  | options:[dimension: 5", 1'-0", etc.]
Glazing Height |  |  | options:[dimension: 2'-1", 3'-0", etc.]

## C - Partitions
C - Partitions
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Framing | Text | N/A | 3-5/8" Metal Studs @ 24"oc, etc |  |  |  | x | x | x
Cladding | Text | N/A | 2-layers Type x GWB |  |  |  | x | x | x
Moisture Resistance | Y/N | N/A |  |  |  |  | x | x | x
Fire Rating | Text | N/A | 2-hr, etc. |  |  |  | x | x | x
Base Constraint |  |  | options:[First Floor, Second Floor, etc.]
Base Offset |  |  | options:[dimension: 6", 1'-4", etc.]
Top Constraint |  |  | options:[First Floor, Second Floor, etc.]
Top Offset |  |  | options:[dimension: 6", 1'-4", etc.]
Structural |  |  | options:[yes, no]
Length |  |  | options:[dimension: 12'-0", 23'-4", etc.]
Area |  |  | options:[area: 110 sf, 1,300 sf, etc.]
Volume |  |  | options:[volume: 1,760 cf, 7,650 cf, etc.]
Mark |  |  | options:[reference to schedule]
Phase Created |  |  | options:[Existing, New Construction, Phase 1, Phase 2, etc.]
Structure Material |  |  | options:[Concrete, Masonry, Wood Stud, Metal Stud, etc.]
Width |  |  | options:[dimension: 4 7/8", 7 1/4" 7 5/8", 1'-0" etc]
Function |  |  | options:[Interior, Exterior, Foundation, Retaining, Soffit, Core-Shaft, etc.]
Model |  |  | options:[manufacturer specific information]
Manufacturer |  |  | options:[manufacturer specific information]
URL |  |  | options:[manufacturer specific information]
Assembly Code (Uniformat) |  |  | C1010
Assembly Description (Uniformat) |  |  | Interior Partitions
Cost |  |  | options:[cost = $/length]
STC Rating |  |  | options:[48, 50, 52, etc.]
UL Number |  |  | options:[419, 910, 914, etc.]
Structural Usage |  |  | options:[Bearing, Shear, Structural Combined, etc.]
Comments |  |  | options:[reference to schedule]
Phase Demolished |  |  | options:[New Construction, Phase 1, Phase 2, etc.]
GWB To Deck |  |  | options:[yes, no]
Stud To Deck |  |  | options:[yes, no]
Insulation To Deck |  |  | options:[yes, no]
Masonry To Deck |  |  | options:[yes, no]
Continuous Reinforcing |  |  | options:[#4 at 16" O.C., #5 at 12" O.C., etc]
Primary Reinforcing |  |  | options:[#4 at 16" O.C., #5 at 12" O.C., etc]
Keynote |  |  | options:[reference to schedule]
Description |  |  | options:[reference to schedule]
Smoke Barrier |  |  | options:[yes, no]
Smoke Partition |  |  | options:[yes, no]

## C - Raised Floor
C - Raised Floor
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Model | Text | N/A | options:[manufacturer specific information] |  |  | x | x | x
Manufacturer | Text | N/A | options:[manufacturer specific information] |  |  | x | x | x
Grid | Text | N/A | 12x12, etc. |  |  | x | x | x
Height | Number |  |  |  |  | x | x | x
Material Thickness | Text | N/A | options:[dimension: 1", 1 1/4",etc.]
Material Types | Text | N/A | options:[Concrete, Steel, Aluminum]
Level |  |  | options:[First Floor, Second Floor, etc.]
Height Offset from Level |  |  | options:[dimension: 8", 1'-0", etc]
Room Bounding |  |  | options:[yes, no]
Structural |  |  | options:[yes, no]
Area |  |  | options:[dimension: 100 sf, 1,235 sf, etc.]
Perimeter |  |  | options:[dimension: 42'-5", 125'-0", etc.]
Comments |  |  | options:[reference to schedule]
Mark |  |  | options:[reference to schedule]
Phase Created |  |  | options:[Existing, New Construction, Phase 1, Phase 2, etc.]
Keynote |  |  | options:[reference to schedule]
URL |  |  | options:[manufacturer specific information]
Assembly Code (Uniformat) |  |  | C1060
Assembly Description (Uniformat) |  |  | Raised Floor Construction
Cost |  |  | options:[cost = $/sf]
Phase Demolished |  |  | options:[New Construction, Phase 1, Phase 2, etc.]

## C - Susp. Clg.
C - Susp. Clg.
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Grid | Text | N/A | 24x24, etc |  |  |  | x | x | x
Material | Text | N/A |  |  |  |  | x | x | x
Seismic Bracing | Y/N | [5 empty] | x | x | x
Phase Created |  |  | options:[Existing, New Construction, Phase 1, Phase 2, etc.]
Material Thickness |  |  | options:[dimension: 3/4", 5/8", etc.]
Model |  |  | options:[manufacturer specific information]
Manufacturer |  |  | options:[manufacturer specific information]
Ceiling Attenuation Class (CAC) |  |  | options:[33, 35, 40, etc.]
Surface Burning Characteristics (SBC) |  |  | options:[ASTM E84, etc.]

## D20 - Plumbing
D20 - Plumbing
Part 1 - Attribute Description | [8 empty] | Part 2 - LOD Profile |  |  |  |  | Part 3 - Example Project-Specific Milestones
[14 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute |  |  |  |  | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Global Attributes
| Component ID |  |  |  | Text |  |  | Part or Equipment Tag |  | x | x | x | x
| Condition Status |  |  |  | Text |  | New, Existing, Demolish, Temporary, User Defined | Status of the element, predominately used in renovation or retrofitting projects |  | x | x | x | x
| Room Number |  |  |  | Text |  |  | Room number where component to be/is installed |  | x | x | x | x
| Room Name |  |  |  | Text |  |  | Room name where component to be/is installed |  |  | x | x | x
| Story Number |  |  |  | Text |  |  | Floor or level room is located |  | x | x | x | x
| Manufacturer Name |  |  |  | Text |  |  | The organization that manufactured and/or assembled the item. |  |  |  | x | x
| Product Name |  |  |  | Text |  |  | The manufacturers model name of the product model (or product line) |  |  |  | x | x
| Model Designation |  |  |  | Text |  |  | The manufacturers model number or designator of the product model (or product line) |  |  |  | x | x
| Component characteristics | [6 empty] | Properties of individual elements of manufactured products
| Acquisition Date |  |  |  | Text |  |  | The date that the manufactured item was purchased.
| Assembly Place |  |  |  | Text |  |  | Code defining where the assembly takes place
| Bar Code |  |  |  | Text |  |  | The identity of the bar code given to an occurrence of the product.
| Batch Reference |  |  |  | Text |  |  | The identity of the batch reference from which an occurrence of a product is taken.
| Production Year |  |  |  | Numeric | Date |  | The year of production of the manufactured item.
| Serial Number |  |  |  | Text |  |  | The serial number assigned to an occurrence of a product.
| Service Life | [6 empty] | Captures the period of time that an artifact will last.
| Mean Time Between Failure |  |  |  | Numeric | Days |  | The average time duration between instances of failure of a product.
| Service Life Duration |  |  |  | Numeric | Years |  | The length or duration of a service life.
| Service Life Factors |  |  |  | Text | `` |  | Captures various factors that impact the expected service life of elements within the system or zone.
| Design Level |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of design level employed.
| Indoor Environment |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the indoor environment (where appropriate).
| In Use Conditions |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the conditions in which components are operating.
| Maintenance Level |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the level or degree of maintenance applied to components.
| Outdoor Environment |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the outdoor environment (where appropriate)
| Quality Of Components |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the quality of components used.
| Work Execution Level |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the quality of work executed.
| Warranty | [6 empty] | A written guarantee, issued to the purchaser of an article by its manufacturer, promising to repair or replace it if necessary within a specified period of time
| Exclusions |  |  |  | Text |  |  | Items, conditions or actions that may be excluded from the warranty or that may cause the warranty to become void.
| Is Extended Warranty |  |  |  | Logic |  | True or False | Indication of whether this is an extended warranty whose duration is greater than that normally assigned
| Point Of Contact |  |  |  | Text |  |  | The organization that should be contacted for action under the terms of the warranty.
| Warranty Content |  |  |  | Text |  |  | The content of the warranty.
| Warranty End Date |  |  |  | Text |  |  | The date on which the warranty expires.
| Warranty Identifier |  |  |  | Text |  |  | The identifier assigned to a warranty.
| Warranty Period |  |  |  | Numeric | Years |  | The time duration during which a manufacturer or supplier guarantees or warrants the performance of an artefact.
| Warranty Start Date |  |  |  | Text |  |  | The date on which the warranty commences.
Fixture-Specific Attributes
|  | Interceptor | [5 empty] | An interceptor is a device designed and installed in order to separate and retain deleterious, hazardous or undesirable matter while permitting normal sewage or liquids to discharge into a collection system by gravity.
|  |  | Cover Length |  | Numeric | Feet |  | The length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the cover |  |  | x | x | x
|  |  | Cover Width |  | Numeric | Feet |  | The length measured along the y-axis in the local coordinate system of the cover |  |  | x | x | x
|  |  | Inlet Connection Size |  | Numeric | Inches |  | Size of the inlet connection. |  | x | x | x | x
|  |  | Nominal Body Depth |  | Numeric | Inches |  | Nominal or quoted =length, measured along the z-axis of the local coordinate system of the object, of the body of the object. |  |  | x | x | x
|  |  | Nominal Body Length |  | Numeric | Inches |  | Nominal or quoted length, measured along the x-axis of the local coordinate system of the object, of the body of the object. |  |  | x | x | x
|  |  | Nominal Body Width |  | Numeric | Inches |  | Nominal or quoted length, measured along the y-axis of the local coordinate system of the object, of the body of the object. |  |  | x | x
|  |  | Outlet Connection Size |  | Numeric | Inches |  | Size of the outlet connection. |  | x | x | x | x
|  |  | Ventilating Pipe Size |  | Numeric | Inches |  | Size of the ventilating pipe(s). |  | x | x | x | x
|  | Bath Tub | [5 empty] | Sanitary appliance for immersion of the human body or parts of it.
|  |  | Bath Type |  | Text |  | Domestic, Domestic Corner, Foot, Jacuzzi, Plunge, Sitz, Treatment, Whirlpool, User Defined | The property enumeration defines the types of bath that may be specified within the property set where. |  | x | x | x | x
|  |  | Color |  | Text |  | White, Almond, User Defined | Principal color of the object. |  |  | x | x | x
|  |  | Drain Size |  | Numeric | Inches |  | The size of the drain outlet connection from the object. |  | x | x | x | x
|  |  | Has Grab Handles |  | Text |  |  | Indicates whether the bath is fitted with handles that provide assistance to a bather in entering or leaving the bath. |  | x | x | x | x
|  |  | Nominal Depth |  | Numeric | Inches |  | Nominal or quoted depth of the object. |  |  | x | x | x
|  |  | Nominal Length |  | Numeric | Inches |  | Nominal or quoted length of the object. |  |  | x | x | x
|  |  | Nominal Width |  | Numeric | Inches |  | Nominal or quoted width of the object. |  |  | x | x | x
|  | Bidet | [5 empty] | Waste water appliance for washing the excretory organs while sitting astride the bowl
|  |  | Color |  | Text |  | White, Almond, User Defined | Color selection for this object. |  |  | x | x | x
|  |  | Drain Size |  | Numeric | Inches |  | The size of the drain outlet connection from the object. |  | x | x | x | x
|  |  | Mounting |  | Text |  | BackToWall, Pedestal, Wall Hung | The property defines sanitary terminals mounting type |  |  | x | x | x
|  |  | Nominal Depth |  | Numeric | Inches |  | Nominal or quoted depth of the object. |  |  | x | x | x
|  |  | Nominal Length |  | Numeric | Inches |  | Nominal or quoted length of the object. |  |  | x | x | x
|  |  | Nominal Width |  | Numeric | Inches |  | Nominal or quoted width of the object. |  |  | x | x | x
|  |  | Spillover Level |  | Numeric | Inches |  | The level at which water spills out of the object. |  |  | x | x | x
|  | Toilet Tank | [5 empty] | A water storage unit attached to a sanitary terminal that is fitted with a device, operated automatically or by the user, that discharges water to cleanse a water closet (toilet) pan, urinal or slop hopper.
|  |  | Tank Capacity |  | Numeric | Gallons |  | Volumetric capacity of the tank |  | x | x | x | x
|  |  | Tank Color |  | Text |  | White, Almond, User Defined | Color of the object. |  |  | x | x | x
|  |  | Tank Height |  | Numeric | Feet | Numeric Value or None | Enumeration that identifies the height of the tank or no tank |  |  | x | x | x
|  |  | Flush Rate |  | Numeric | Gallons |  | The minimum and maximum volume of water used at each flush. |  | x | x | x | x
|  |  | Flush Type |  | Text |  | Lever, Pull, Push, Sensor, User Defined | The types of flushing mechanism that may be specified for tanks and sanitary terminals |  |  | x | x | x
|  |  | Is Automatic Flush |  | Logic |  | True or False | Value that determines if the tank is flushed automatically either after each use or periodically |  |  | x | x | x
|  |  | Is Single Flush |  | Logic |  | True or False | Indicates whether the tank is single flush |  |  | x | x | x
|  | Toilet Bowl | [5 empty] | Soil appliance for the disposal of excrement.
|  |  | Color |  | Text |  | White, Almond, User Defined | Color selection for this object |  |  | x | x | x
|  |  | Nominal Depth |  | Numeric | Inches |  | Nominal or quoted depth of the object. |  |  | x | x | x
|  |  | Nominal Length |  | Numeric | Inches |  | Nominal or quoted length of the object. |  |  | x | x | x
|  |  | Nominal Width |  | Numeric | Inches |  | Nominal or quoted width of the object. |  |  | x | x | x
|  |  | Pan Mounting |  | Text |  | BackToWall, Pedestal, WallHung, User Defined | The property defines the forms of mounting or fixing of the sanitary terminal |  | x | x | x | x
|  |  | Spillover Level |  | Numeric | Inches |  | The level at which water spills out of the terminal. |  |  | x | x | x
|  |  | Toilet Pan Type |  | Text |  | Siphonic, Squat, WashDown, WashOut, User Defined | The property defines the types of toilet pan |  | x | x | x | x
|  |  | Toilet Type |  | Text |  | BedPanWasher, Chemical, CloseCoupled, LooseCoupled, SlopHopper, User Defined | Enumeration that defines the types of toilet (water closet) arrangement |  | x | x | x | x
|  | Urinal | [5 empty] | Soil appliance that receives urine and directs it to a waste outlet.
|  |  | Color |  | Text |  | White, Almond, User Defined | Color of the urinal. |  |  | x | x | x
|  |  | Mounting |  | Text |  | BackToWall, Pedestal, WallHung, User Defined | Selection of the form of mounting |  | x | x | x | x
|  |  | Nominal Depth |  | Numeric | Inches |  | Nominal or quoted depth of the object. |  |  | x | x | x
|  |  | Nominal Length |  | Numeric | Inches |  | Nominal or quoted length of the object. |  |  | x | x | x
|  |  | Nominal Width |  | Numeric | Inches |  | Nominal or quoted width of the object. |  |  | x | x | x
|  |  | Spillover Level |  | Numeric | Inches |  | The level at which water spills out of the object. |  |  | x | x | x
|  |  | Urinal Type |  | Text |  | Bowl, Slab, Stall, Trough, Wall Mounted, User Defined | Selection of the type of urinal |  | x | x | x | x
|  | Drinking Fountain | [5 empty] | A sanitary terminal that provides a low pressure jet of water for a specific purpose.
|  |  | Color |  | Text |  | White, Almond, Stainless, User Defined | Color selection for this object. |  |  | x | x | x
|  |  | Drain Size |  | Numeric | Inches |  | The size of the drain outlet connection from the object. |  | x | x | x | x
|  |  | Fountain Type |  | Text |  | DrinkingWater, Eyewash, User Defined | Selection of the type of fountain |  | x | x | x | x
|  |  | Mounting |  | Text |  | BackToWall, Pedestal, CounterTop, WallHung, User Defined | Selection of the form of mounting of the fountain |  | x | x | x | x
|  |  | Nominal Depth |  | Numeric | Inches |  | Nominal or quoted depth of the object. |  |  | x | x | x
|  |  | Nominal Length |  | Numeric | Inches |  | Nominal or quoted length of the object. |  |  | x | x | x
|  |  | Nominal Width |  | Numeric | Inches |  | Nominal or quoted width of the object. |  |  | x | x | x
|  | Shower | [5 empty] | Installation or waste water appliance that emits a spray of water to wash the human body.
|  |  | Color |  | Text |  | White, Almond, User Defined | Color selection for this object. |  |  | x | x
|  |  | Drain Size |  | Numeric | Inches |  | The size of the drain outlet connection from the object. |  | x | x | x | x
|  |  | Has Tray |  | Logic |  | True or False | Indicates whether the shower has a separate receptacle that catches the water in a shower and directs it to a waste outlet. |  | x | x | x | x
|  |  | Nominal Depth |  | Numeric | Inches |  | Nominal or quoted depth of the object. |  |  | x | x | x
|  |  | Nominal Length |  | Numeric | Inches |  | Nominal or quoted length of the object. |  |  | x | x | x
|  |  | Nominal Width |  | Numeric | Inches |  | Nominal or quoted width of the object. |  |  | x | x | x
|  |  | Shower Head Description |  | Text |  |  | A description of the shower head(s) that emit the spray of water. |  | x | x | x | x
|  |  | Shower Type |  | Text |  | Drench, Individual, Tunnel, User Defined | Selection of the type of shower |  | x | x | x | x
|  | Sink or Lavatory | [5 empty] | Waste water appliance for receiving, retaining or disposing of domestic, culinary, laboratory or industrial process liquids.
|  |  | Color |  | Text |  | White, Almond, User Defined | Color selection for this object. |  |  | x | x | x
|  |  | Drain Size |  | Numeric | Inches |  | The size of the drain outlet connection from the object. |  | x | x | x | x
|  |  | Mounting |  | Text |  | BackToWall, Pedestal, CounterTop, WallHung, User Defined | Selection of the form of mounting of the sink |  | x | x | x | x
|  |  | Mounting Offset |  | Text |  |  | For counter top mounted sinks, the vertical offset between the top of the sink and the counter top. |  | x | x | x | x
|  |  | Nominal Depth |  | Numeric | Inches |  | Nominal or quoted depth of the object. |  |  | x | x | x
|  |  | Nominal Length |  | Numeric | Inches |  | Nominal or quoted length of the object. |  |  | x | x | x
|  |  | Nominal Width |  | Numeric | Inches |  | Nominal or quoted width of the object. |  |  | x | x | x
|  |  | Sink Type |  | Text |  | Belfast, Bucket, Cleaners, Combination_Left, Combination_Right, Combination_Double, Drip, Laboratory, Plaster, Pot, Rinsing, Preparation, Bar, User Defined | Selection of the type of sink |  | x | x | x | x
|  | Wash Basin or Lavatory | [5 empty] | Waste water appliance for washing the upper parts of the body.
|  |  | Color |  | Text |  | White, Almond, User Defined | Color of the object. |  |  | x | x | x
|  |  | Drain Size |  | Numeric | Inches |  | The size of the drain outlet connection from the object. |  | x | x | x | x
|  |  | Mounting |  | Text |  | BackToWall, Pedestal, CounterTop, WallHung, User Defined | Selection of the form of mounting |  | x | x | x | x
|  |  | Mounting Offset |  | Numeric | Inches |  | For counter top mounted basins the vertical offset between the top of the sink and the counter top. |  |  | x | x | x
|  |  | Nominal Depth |  | Numeric | Inches |  | Nominal or quoted depth of the object. |  |  | x | x | x
|  |  | Nominal Length |  | Numeric | Inches |  | Nominal or quoted length of the object. |  |  | x | x | x
|  |  | Nominal Width |  | Numeric | Inches |  | Nominal or quoted width of the object.
|  |  | Wash Hand Basin Type |  | Text |  | DentalCuspidor, HandRinse, Hospital, Tipup, Vanity, Washfountain, WashingTrough, User Defined | Defines the types of wash hand basin
|  |  | Reference |  | Text |  |  | Reference ID for this specified type in this project (e.g. type 'A-1'), provided, if there is no classification reference to a recognized classification system used.
|  | Waste Floor Trap | [5 empty] | Pipe fitting, set into the floor, that retains liquid to prevent the passage of foul air.
|  |  | Cover Length |  | Numeric | Inches |  | The length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the cover |  |  | x | x | x
|  |  | Cover Width |  | Numeric | Inches |  | The length measured along the y-axis in the local coordinate system of the cover of the trap. |  |  | x | x | x
|  |  | Cover Material |  | Text |  | SS, Aluminum, User Defined | Material from which the cover or grating is constructed. |  |  | x | x | x
|  |  | Has Strainer |  | Logic |  | True or False | Indicates whether the trap has a strainer |  | x | x | x | x
|  |  | Inlet Connection Size |  | Numeric | Inches |  | Size of the inlet connection(s) |  | x | x | x | x
|  |  | Inlet Pattern Type |  | Text |  | 0,1,2,3 or 4: inlet connections and arrangement may vary. The outlet is either vertical or is placed at the bottom (south side) of the trap (when viewed in plan). Position 1 is to the left (west), position 2 is to the top (north), position 3 is to the right (east) and position 4 is to the bottom (south). | Identifies the pattern of inlet connections to a trap |  | x | x | x | x
|  |  | Is For Grey Water |  | Logic |  | True or False | Indicates if the purpose of the floor trap is to receive grey water |  | x | x | x | x
|  |  | Nominal Body Depth |  | Numeric | Inches |  | Nominal or quoted length measured along the z-axis in the local coordinate system of the chamber of the trap. |  |  | x | x | x
|  |  | Nominal Body Length |  | Numeric | Inches |  | Nominal or quoted length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the chamber of the trap. |  |  | x | x | x
|  |  | Nominal Body Width |  | Numeric | Inches |  | Nominal or quoted length measured along the y-axis in the local coordinate system of the chamber of the trap. |  |  | x | x | x
|  |  | Outlet Connection Size |  | Numeric | Inches |  | Size of the outlet connection from the object. |  | x | x | x | x
|  |  | Spillover Level |  | Numeric | Inches |  | The level at which water spills out of the terminal. |  |  | x | x | x
|  |  | Trap Type |  | Text |  |  | Identifies the predefined types of waste trap used in combination with the floor trap from which the type required may be set. |  | x | x | x | x
|  | Floor Drain | [5 empty] | Pipe fitting, set into the floor, that collects waste water and discharges it to a separate trap.
|  |  | Cover Length |  | Numeric | Inches |  | The length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the cover |  |  | x | x | x
|  |  | Cover Width |  | Numeric | Inches |  | The length measured along the y-axis in the local coordinate system of the cover of the waste. |  |  | x | x | x
|  |  | Nominal Body Depth |  | Numeric | Inches |  | Nominal or quoted length measured along the z-axis in the local coordinate system of the waste. |  |  | x | x | x
|  |  | Nominal Body Length |  | Numeric | Inches |  | Nominal or quoted length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the waste. |  |  | x | x | x
|  |  | Nominal Body Width |  | Numeric | Inches |  | Nominal or quoted length measured along the y-axis in the local coordinate system of the waste. |  |  | x | x | x
|  |  | Outlet Connection Size |  | Numeric | Inches |  | Size of the outlet connection from the object. |  | x | x | x | x
|  | Floor Sink | [5 empty] | Pipe fitting or assembly of fittings to receive surface water or waste water, fitted with a grating or sealed cover.
|  |  | Back Inlet Pattern Type |  | Text |  | 0,1,2,3 or 4: inlet connections and arrangement may vary. The outlet is either vertical or is placed at the bottom (south side) of the trap (when viewed in plan). Position 1 is to the left (west), position 2 is to the top (north), position 3 is to the right (east) and position 4 is to the bottom (south). | Identifies the pattern of inlet connections to a trap |  | x | x | x | x
|  |  | Cover Length |  | Numeric | Inches |  | The length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the cover of the trap. |  |  | x | x | x
|  |  | Cover Width |  | Numeric | Inches |  | The length measured along the y-axis in the local coordinate system of the cover of the trap. |  |  | x | x | x
|  |  | Sink Type |  | Text |  |  | Identifies the predefined types of sink from which the type required may be set. |  | x | x | x | x
|  |  | Inlet Connection Size |  | Numeric | Inches |  | Size of the inlet connection(s) |  | x | x | x | x
|  |  | Nominal Sump Depth |  | Numeric | Inches |  | Nominal or quoted length measured along the z-axis in the local coordinate system of the sump. |  |  | x | x | x
|  |  | Nominal Sump Length |  | Numeric | Inches |  | Nominal or quoted length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the sump. |  |  | x | x | x
|  |  | Nominal Sump Width |  | Numeric | Inches |  | Nominal or quoted length measured along the y-axis in the local coordinate system of the sump. |  |  | x | x | x
|  |  | Outlet Connection Size |  | Numeric | Inches |  | Size of the outlet connection from the object. |  | x | x | x | x
|  |  | Trap Type |  | Text |  |  | Identifies the predefined types of trap from which the type required may be set. |  | x | x | x | x
|  | Floor Trap | [5 empty] | Pipe fitting or assembly of fittings to receive surface water or waste water, fitted with a grating or sealed cover and discharging through a trap
|  |  | Back Inlet Pattern Type |  | Text |  | 0,1,2,3 or 4: inlet connections and arrangement may vary. The outlet is either vertical or is placed at the bottom (south side) of the trap (when viewed in plan). Position 1 is to the left (west), position 2 is to the top (north), position 3 is to the right (east) and position 4 is to the bottom (south). | Identifies the pattern of inlet connections to a trap |  | x | x | x | x
|  |  | Cover Length |  | Numeric | Inches |  | The length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the cover |  |  | x | x | x
|  |  | Cover Width |  | Numeric | Inches |  | The length measured along the y-axis in the local coordinate system of the cover of the trap. |  |  | x | x | x
|  |  | Sink Type |  | Text |  |  | Identifies the predefined types of sink from which the type required may be set. |  | x | x | x | x
|  |  | Has Strainer |  | Logic |  | True or False | Indicates whether the trap has a strainer |  | x | x | x | x
|  |  | Inlet Connection Size |  | Numeric | Inches |  | Size of the inlet connection(s) |  | x | x | x | x
|  |  | Nominal Body Depth |  | Numeric | Inches |  | Nominal or quoted length measured along the z-axis in the local coordinate system of the chamber of the trap. |  |  | x | x | x
|  |  | Nominal Body Length |  | Numeric | Inches |  | Nominal or quoted length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the chamber of the trap. |  |  | x | x | x
|  |  | Nominal Body Width |  | Numeric | Inches |  | Nominal or quoted length measured along the y-axis in the local coordinate system of the chamber of the trap. |  |  | x | x | x
|  |  | Outlet Connection Size |  | Numeric | Inches |  | Size of the outlet connection from the object. |  | x | x | x | x
|  |  | Trap Type |  | Text |  |  | Identifies the predefined types of trap from which the type required may be set. |  | x | x | x | x
|  | Roof Drain | [5 empty] | Pipe fitting, set into the roof, that collects rainwater for discharge into the rainwater system.
|  |  | Cover Length |  | Numeric | Inches |  | The length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the cover |  |  | x | x | x
|  |  | Cover Width |  | Numeric | Inches |  | The length measured along the y-axis in the local coordinate system of the cover of the drain. |  |  | x | x | x
|  |  | Nominal Body Depth |  | Numeric | Inches |  | Nominal or quoted length measured along the z-axis in the local coordinate system of the drain. |  |  | x | x | x
|  |  | Nominal Body Length |  | Numeric | Inches |  | Nominal or quoted length measured along the x-axis in the local coordinate system or the radius (in the case of a circular shape in plan) of the drain. |  |  | x | x | x
|  |  | Nominal Body Width |  | Numeric | Inches |  | Nominal or quoted length measured along the y-axis in the local coordinate system of the drain. |  |  | x | x | x
|  |  | Outlet Connection Size |  | Numeric | Inches |  | Size of the outlet connection from the object. |  | x | x | x | x
|  | Garbage Disposal | [5 empty] | Electrically operated device that reduces kitchen or other waste into fragments small enough to be flushed into a drainage system.
|  |  | Drain Connection Size |  | Numeric | Inches |  | Size of the drain connection inlet to the waste disposal unit. |  | x | x | x | x
|  |  | Nominal Depth |  | Numeric | Inches |  | Nominal or quoted depth of the object measured from the inlet drain connection to the base of the unit. |  |  | x | x | x
|  |  | Outlet Connection Size |  | Numeric | Inches |  | Size of the outlet connection from the waste disposal unit. |  | x | x | x | x
|  | Waste Trap | [5 empty] | Pipe fitting, set adjacent to a sanitary terminal, that retains liquid to prevent the passage of sewer gases
|  |  | Inlet Connection Size |  | Numeric | Inches |  | Size of the inlet connection(s) |  | x | x | x | x
|  |  | Outlet Connection Size |  | Numeric | Inches |  | Size of the outlet connection from the object. |  | x | x | x | x
|  |  | Waste Trap Type |  | Text |  |  | Identifies the predefined types of trap from which the type required may be set. |  | x | x | x | x
|  | Water Filter | [5 empty] | A filter is an apparatus used to remove particulate or gaseous matter from fluids and gases
|  |  | Water Filter Type |  | Text |  | Filtration, Purification, Softening, User Defined | Identifies the type of water filter |  | x | x | x | x
|  | Flow Meter | [5 empty] | A flow meter is a device that is used to measure the flow rate in a system.
|  |  | Purpose |  | Text |  |  | Enumeration defining the purpose of the flow meter occurrence. |  | x | x | x | x
|  |  | Read Out Type |  | Text |  | Mechanical, CombinationPulser-Mechanical, Magnetic Sensor, witch Pulsers: Type "V" and "W" switch closures (reed switches) have a solid cover without a window for viewing the single counter. Type "V" provides one pulse output and type "W" provides dual simultaneous outputs. Type "F" LCD Displays: | Indication of the form that readout from the meter take |  | x | x | x | x
|  |  | Remote Reading |  | Text |  | MechanicalTotalizers, CombinationPulser-Mechanical Totalizer, MagneticSensor, Mechanical Totalizer, Switch Pulsers, LCDDisplays, User Defined: | Indicates whether the meter has a connection for remote reading through connection of a communication device (set TRUE) or not (set FALSE). |  | x | x | x | x
|  |  | Energy Meter |  |  |  |  | Device that measures, indicates and sometimes records, the energy usage in a system.
|  |  |  | Maximum Current | Numeric | Amps |  | The maximum allowed current that a device is certified to handle. |  | x | x | x | x
|  |  |  | Multiple Tariff | Logic |  | True or False | Indicates whether meter has built-in support for multiple tariffs (variable energy cost rates). |  |  | x | x
|  |  |  | Nominal Current | Numeric | Amps |  | The nominal current that is designed to be measured. |  | x | x | x | x
|  |  | Gas Meter |  |  |  |  | Device that measures, indicates and sometimes records, the volume of gas that passes through it without interrupting the flow.
|  |  |  | Connection Size | Numeric | Inches |  | Defines the size of inlet and outlet pipe connections to the meter. |  | x | x | x | x
|  |  |  | Gas Type | Text |  |  | Defines the types of gas that may be specified. |  | x | x | x | x
|  |  |  | Maximum Flow Rate | Numeric | Cubic Feet per Minute |  | Maximum rate of flow which the meter is expected to pass. |  | x | x | x | x
|  |  |  | Maximum Pressure Loss | Numeric | PSI |  | Pressure loss expected across the meter under conditions of maximum flow. |  | x | x | x | x
|  |  | Oil Meter |  |  |  |  | Device that measures, indicates and sometimes records, the volume of oil that passes through it without interrupting the flow.
|  |  |  | Connection Size | Numeric | Inches |  | Defines the size of inlet and outlet pipe connections to the meter. |  | x | x | x | x
|  |  |  | Maximum Flow Rate | Numeric | Gallons per Minute |  | Maximum rate of flow which the meter is expected to pass. |  | x | x | x | x
|  |  | Water Meter |  |  |  |  | Device that measures, indicates and sometimes records, the volume of water that passes through it without interrupting the flow.
|  |  |  | Backflow Preventer Type | Text |  |  | Identifies the type of backflow preventer installed |  | x | x | x | x
|  |  |  | Connection Size | Numeric | Inches |  | Defines the size of inlet and outlet pipe connections to the meter. |  | x | x | x | x
|  |  |  | Maximum Flow Rate | Numeric | Gallons per Minute |  | Maximum rate of flow which the meter is expected to pass. |  | x | x | x | x
|  |  |  | Maximum Pressure Loss | Numeric | PSI |  | Pressure loss expected across the meter under conditions of maximum flow. |  | x | x | x | x
|  |  |  | Type | Text |  |  | Defines the allowed values for selection of the flow meter operation type. |  | x | x | x | x
|  | Heat Exchanger | [5 empty] | A heat exchanger is a device used to provide heat transfer between non-mixing media such as plate and shell and tube heat exchangers.
|  |  | Arrangement |  | Text |  | Counterflow, Crossflow, Parallelflow, Multipass, User Defined | Defines the basic flow arrangements for the heat exchanger |  | x | x | x | x
|  |  | Plate Exchanger |  |  |  |  | Common attributes of plate heat exchanger
|  |  |  | Number Of Plates | Numeric | None | 1,2,3,… | Number of plates used by the plate heat exchanger.
|  | Culvert | [5 empty] | Covered channel or large pipe that forms a watercourse below ground level, usually under a road or railway.
|  |  | Clear Depth |  | Numeric | Inches |  | The clear depth of the culvert. |  |  | x | x | x
|  |  | Internal Width |  | Numeric | Inches |  | The internal width of the culvert. |  |  | x | x | x
|  | Gutter | [5 empty] | Gutter segment type common attributes.
|  |  | Flow Rating |  | Numeric | Gallons per Minute |  | Actual flow capacity for the gutter. Value of 0.00 means this value has not been set. |  | x | x | x | x
|  |  | Slope |  | Numeric | Degrees |  | Angle of the gutter to allow for drainage. |  | x | x | x | x
|  | Pump | [5 empty] | A pump is a device which imparts mechanical work on fluids or slurries to move them through a channel or pipeline.
|  |  | Base Type |  | Text |  | Frame, Base, None, User Defined | Defines general types of pump bases |  | x | x | x | x
|  |  | Drive Connection Type |  | Text |  | Directdrive, Beltdrive, Coupling, User Defined | The way the pump drive mechanism is connected to the pump |  | x | x | x | x
|  |  | Impeller Diameter |  | Numeric | Inches |  | Diameter of pump impeller |  | x | x | x | x
|  |  | Flowrate |  | Numeric | Gallons per Minute |  | The actual operational fluid flowrate. |  | x | x | x | x
|  |  | Mechanical Efficiency |  | Numeric | Percent |  | The pumps operational mechanical efficiency. |  | x | x | x | x
|  |  | Overall Efficiency |  | Numeric | Percent |  | The pump and motor overall operational efficiency. |  | x | x | x | x
|  |  | Power |  | Numeric | Horsepower |  | The actual power consumption of the pump. |  | x | x | x | x
|  |  | Pressure Rise |  | Numeric | PSI |  | The developed pressure. |  | x | x | x | x
|  |  | Rotation Speed |  | Numeric | RPM |  | Pump rotational speed. |  | x | x | x | x
|  |  | Connection Size |  | Numeric | Inches |  | The connection size of the to and from the pump. |  | x | x | x | x
|  |  | Flow Rate Range |  | Numeric | Gallons per Minute |  | Allowable range of volume of fluid being pumped against the resistance specified. |  | x | x | x | x
|  |  | Flow Resistance Range |  | Numeric | PSI |  | Allowable range of frictional resistance against which the fluid is being pumped. |  | x | x | x | x
|  |  | Net Positive Suction Head |  | Numeric | Feet or PSI |  | Minimum liquid pressure at the pump inlet to prevent cavitation. |  | x | x | x | x
|  |  | Nominal Rotation Speed |  | Numeric | RPM |  | Pump rotational speed under nominal conditions. |  | x | x | x | x
|  |  | Temperature Range |  | Numeric | Degrees F |  | Allowable operational range of the fluid temperature. |  | x | x | x
|  | Tank | [5 empty] | A tank is a vessel or container in which a fluid or gas is stored for later use
|  |  | Has Ladder |  | Logic |  | True or False | Indication of whether the tank is provided with a ladder |  | x | x | x | x
|  |  | Has Visual Indicator |  | Logic |  | True or False | Indication of whether the tank is provided with a visual indicator |  | x | x | x | x
|  |  | Tank Composition |  | Text |  | Complex, Element, Partial, User Defined | Defines the level of element composition where |  | x | x | x | x
|  |  | Access Type |  | Text |  | Manhole, User Defined | Defines the types of access (or cover) to a tank that may be specified |  |  | x | x | x
|  |  | Effective Capacity |  | Numeric | Gallons |  | The total effective or actual volumetric capacity of the tank. |  | x | x | x | x
|  |  | End Shape Type |  | Text |  | Semi-Elliptical, ASMEFlanged_Dished, ASMEHighCrown, ConicalDished, StndardFlanged_Dished, FlangedOnly, DishedOnly, User Defined | Defines the types of end shapes that can be used for preformed tanks |  | x | x | x | x
|  |  | First Curvature Radius |  | Numeric | Inches/Feet |  | FirstCurvatureRadius should be defined as the base or left side radius of curvature value. |  |  | x | x | x
|  |  | Nominal Capacity |  | Numeric | Gallons |  | The total nominal or design volumetric capacity of the tank. |  | x | x | x | x
|  |  | Nominal Depth |  | Numeric | Feet |  | The nominal depth of the tank. Note: Not required for a horizontal cylindrical tank. |  |  | x | x | x
|  |  | Nominal Length Or Diameter |  | Numeric | Feet |  | The nominal length or, in the case of a vertical cylindrical tank, the nominal diameter of the tank. |  |  | x | x | x
|  |  | Nominal Width Or Diameter |  | Numeric | Feet |  | The nominal width or, in the case of a horizontal cylindrical tank, the nominal diameter of the tank. Note: Not required for a vertical cylindrical tank. |  |  | x | x | x
|  |  | Number Of Sections |  | Numeric | None | 1,2,3.. | Number of sections used in the construction of the tank. Default is 1. Note: All sections assumed to be the same size. |  |  | x | x | x
|  |  | Operating Weight |  | Numeric | Lbs |  | Operating weight of the tank including all of its contents. |  | x | x | x | x
|  |  | Pattern Type |  | Text |  |  | Defines the types of pattern (or shape of a tank that may be specified. |  | x | x | x | x
|  |  | Second Curvature Radius |  | Numeric | Inches/Feet |  | SecondCurvatureRadius should be defined as the top or right side radius of curvature value. |  |  | x | x | x
|  |  | Storage Type |  | Text |  |  | Defines the general material category intended to be stored. |  | x | x | x | x
|  |  | Expansion Tank |  |  |  |  | Common attributes of an expansion type tank.
|  |  |  | Charge Pressure | Numeric | PSI |  | Nominal or design operating pressure of the tank. |  | x | x | x | x
|  |  |  | Pressure Regulator Setting | Numeric | PSI |  | Pressure that is automatically maintained in the tank. |  | x | x | x | x
|  |  |  | Relief Valve Setting | Numeric | PSI |  | Pressure at which the relief valve activates. |  | x | x | x | x
|  |  | Manufactured Tank |  |  |  |  | Fixed vessel manufactured as a single unit with one or more compartments for storing a liquid.
|  |  |  | End Shape Type | Text |  | Semi-Elliptical, ASMEFlanged_Dished, ASMEHighCrown, ConicalDished, StndardFlanged_Dished, FlangedOnly, DishedOnly, User Defined | Defines the types of end shapes that can be used for preformed tanks |  | x | x | x | x
|  |  |  | First Curvature Radius | Numeric | Feet |  | FirstCurvatureRadius should be defined as the base or left side radius of curvature value. |  |  | x | x | x
|  |  |  | Pattern Type | Text |  |  | Defines the types of pattern or shape of a tank that may be specified. |  | x | x | x | x
|  |  |  | Second Curvature Radius | Numeric | Feet |  | SecondCurvatureRadius should be defined as the top or right side radius of curvature value. |  |  | x | x | x
|  |  | Pressure Vessel |  |  |  |  | Common attributes of a pressure vessel.
|  |  |  | Charge Pressure | Numeric | PSI |  | Nominal or design operating pressure of the tank. |  | x | x | x | x
|  |  |  | Pressure Regulator Setting | Numeric | PSI |  | Pressure that is automatically maintained in the tank. |  | x | x | x | x
|  |  |  | Relief Valve Setting | Numeric | PSI |  | Pressure at which the relief valve activates. |  | x | x | x
|  |  |  | Number Of Sections | Numeric | None | 1,2,3.. | Number of sections used in the construction of the tank Note: All sections assumed to be the same size. |  |  | x | x | x
|  |  |  | Section Length | Numeric | Feet |  | The length of a section used in the construction of the tank. |  |  | x | x | x
|  |  |  | Section Width | Numeric | Feet |  | The width of a section used in the construction of the tank. |  |  | x | x | x
|  | Valve | [5 empty] | A valve is used in a building services piping distribution system to control or modulate the flow of the fluid.
|  |  | Measured Flow Rate |  | Numeric | GPM |  | The rate of flow of a fluid measured across the valve. |  | x | x | x | x
|  |  | Measured Pressure Drop |  | Numeric | PSI |  | The actual pressure drop in the fluid measured across the valve. |  | x | x | x | x
|  |  | Percentage Open |  | Numeric | % |  | The ratio between the amount that the valve is open to the full open position of the valve. |  | x | x | x | x
|  |  | Body Material |  | Text |  |  | Material from which the body of the valve is constructed. |  | x | x | x | x
|  |  | Close Off Rating |  | Numeric | PSI |  | Close off rating. |  | x | x | x | x
|  |  | Flow Coefficient |  | Numeric | Kv or Cv |  | Flow coefficient |  | x | x | x | x
|  |  | Size |  | Numeric | Inches |  | The size of the connection to the valve (or to each connection for faucets, mixing valves, etc.). |  | x | x | x | x
|  |  | Test Pressure |  | Numeric | PSI |  | The maximum pressure to which the valve has been subjected under test. |  | x | x | x
|  |  | Valve Mechanism |  | Text |  | Ball, Butterfly, Gate, Globe, Plug, Gland, Needle | The mechanism by which the valve function is achieved |  | x | x | x | x
|  |  | Valve Operation |  | Text |  | Dropweight, Float, Hydraulic, Lever, Lockshield, Motorized, Pneumatic, Solenoid, Thermostatic, Wheel , User Defined | The method of valve operation |  | x | x | x | x
|  |  | Valve Pattern |  |  |  | Singleport, Angled_2 Port, Straight_2_Port, Straight_3 _Port, Crossover_4_Port | The configuration of the ports of a valve according to either the linear route taken by a fluid flowing through the valve or by the number of ports |  | x | x | x | x
|  |  | Working Pressure |  | Numeric | PSI |  | The normally expected maximum working pressure of the valve. |  | x | x | x | x
|  |  | Air Vent |  | Text |  |  | Valve used to release air from a pipe or fitting. Note that an air release valve is constrained to have a single port pattern
|  |  | Is Automatic |  | Logic |  | True or False | Indication of whether the valve is automatically operated
|  |  | Faucet |  | Text |  |  | A small diameter valve, with a free outlet, from which water is drawn.
|  |  | Faucet Function |  | Text |  |  | Defines the operating temperature of a faucet that may be specified.
|  |  | Faucet Operation |  | Text |  | CeramicDisc, LeverHandle, NonConcussiveSelfClosing, QuarterTurn, QuickAction, ScrewDown, SelfClosing, TimedSelfClosing, User Defined | Defines the range of ways in which a faucet can be operated that may be specified
|  |  | Faucet Top Description |  | Text |  |  | Description of the operating mechanism/top of the faucet.
|  |  | Faucet Type |  | Text |  | Bib, Globe, Diverter, DividedFlowCombination, Pillar, SngleOutletCombination, Spray, SprayMixing, | Defines the range of faucet types that may be specified
|  |  | Finish |  | Text |  | Chrome, Bronze, User Defined | Description of the finish applied to the faucet.
|  |  | Flush Valve |  | Text |  |  | Valve that flushes a predetermined quantity of water to cleanse a WC, urinal or slop hopper. Note that a flushing valve is constrained to have a 2 port pattern.
|  |  | Flushing Rate |  | Numeric | GPM |  | The predetermined quantity of water to be flushed.
|  |  | Has Integral Shut Off Device |  | Logic |  | True or False | Indication of whether the flushing valve has an integral shut off device fitted
|  |  | Is High Pressure |  | Logic |  | True or False | Indication of whether the flushing valve is suitable for use on a high pressure water main
|  |  | Gas Tap Valve |  | Text |  |  | A small diameter valve, used to discharge gas from a system.
|  |  | Has Hose Union |  | Logic |  | True or False | Indicates whether the gas tap is fitted with a hose union connection
|  |  | Hose Bib |  | Text |  |  | A small diameter valve, used to drain water from a tank or water filled system.
|  |  | Has Hose Union |  | Logic |  | True or False | Indicates whether the drawoff cock is fitted with a hose union connection
|  |  | Isolation Valve |  | Text |  |  | Valve that is used to isolate system components. Note that an isolating valve is constrained to have a 2 port pattern.
|  |  | Is Normally Open |  | Logic |  | True or False | If TRUE, the valve is normally open. If FALSE is normally closed.
|  |  | Isolating Purpose |  | Text |  |  | Defines the purpose for which the isolating valve is used since the way in which the valve is identified as an isolating valve may be in the context of its use.
|  |  | Mixing Valve |  | Text |  |  | A valve where typically the temperature of the outlet is determined by mixing hot and cold water inlet flows.
|  |  | Mixer Control |  | Text |  |  | Defines the form of control of the mixing valve.
|  |  | Outlet Connection Size |  | Numeric | Inches |  | The size of the pipework connection from the mixing valve.
|  |  | Pressure Reducing Valve |  | Text |  |  | Valve that reduces the pressure of a fluid immediately downstream of its position in a pipeline to a preselected value or by a predetermined ratio. Note that a pressure reducing valve is constrained to have a 2 port pattern.
|  |  | Downstream Pressure |  | Numeric | Imperial |  | The operating pressure of the fluid downstream of the pressure reducing valve.
|  |  | Upstream Pressure |  | Numeric | Imperial |  | The operating pressure of the fluid upstream of the pressure reducing valve.
|  |  | Pressure Relief Valve |  | Text |  |  | Spring or weight loaded valve that automatically discharges to a safe place fluid that has built up to excessive pressure in pipes or fittings. Note that a pressure relief valve is constrained to have a single port pattern.
|  |  | Relief Pressure |  | Numeric | Imperial |  | The pressure at which the spring or weight in the valve is set to discharge fluid.
|  | Vibration Isolator | [5 empty] | A vibration isolator is a device used to minimize the effects of vibration transmissibility in a building
|  |  | Height |  | Numeric | Inches |  | Height of the vibration isolator before the application of load. |  |  | x | x | x
|  |  | Isolator Compressibility |  | Text |  |  | The compressibility of the vibration isolator. |  | x | x | x | x
|  |  | Isolator Static Deflection |  | Numeric | Inches |  | Static deflection of the vibration isolator. |  | x | x | x | x
|  |  | Maximum Supported Weight |  | Numeric | Lbs |  | The maximum weight that can be carried by the vibration isolator. |  |  | x | x | x
|  |  | Vibration Transmissibility |  | Numeric | % |  | The vibration transmissibility percentage. |  | x | x | x | x
Note on B12: Author: name change From Model Label To : Product Name
Note on B13: Author: Changed Name From Model Reference To Model Designation

## D30 - HVAC
D30 - HVAC
Part 1 - Attribute Description | [8 empty] | Part 2 - LOD Profile |  |  |  |  | Part 3 - Example Project-Specific Milestones
[14 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute |  |  |  |  | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Global Attributes
| Component ID |  |  |  | Text |  |  | Project assigned number for components (e.g. tag number) |  | x | x | x | x
| Condition Status |  |  |  | Text |  | New, Existing, Demolish, Temporary, User Defined | Status of the element, predominately used in renovation or retrofitting projects |  | x | x | x | x
| Room Number |  |  |  | Text |  |  | Room number where component to be/is installed |  | x | x | x | x
| Room Name |  |  |  | Text |  |  | Room name where component to be/is installed |  |  | x | x | x
| Story Number |  |  |  | Text |  |  | Floor or level room is located |  | x | x | x | x
| Manufacturer Name |  |  |  | Text |  |  | The organization that manufactured and/or assembled the item. |  |  |  | x | x
| Product Name |  |  |  | Text |  |  | The descriptive model name of the product model (or product line) as assigned by the manufacturer of the manufactured item. |  |  |  | x | x
| Model Designation |  |  |  | Text |  |  | The model number or designator of the product model (or product line) as assigned by the manufacturer of the manufactured item. |  |  |  | x | x
| Component characteristics | [6 empty] | Defines properties of individual instances of manufactured products that may be given by the manufacturer.
| Acquisition Date |  |  |  | Text | Date |  | The date that the manufactured item was purchased.
| Assembly Place |  |  |  | Text |  | Onsite, factory, other offsite location | Enumeration defining where the assembly is intended to take place, either in a factory, other offsite location or on the building site.
| Bar Code |  |  |  | Text |  |  | The identity of the bar code given to an occurrence of the product.
| Batch Reference |  |  |  | Text |  |  | The identity of the batch reference from which an occurrence of a product is taken.
| Production Year |  |  |  | Numeric | Year |  | The year of production of the manufactured item.
| Serial Number |  |  |  | Text |  |  | The serial number assigned to an occurrence of a product.
| Service Life | [6 empty] | Captures the period of time that an artifact will last.
| Mean Time Between Failure |  |  |  | Numeric | Days |  | The average time duration between instances of failure of a product.
| Service Life Duration |  |  |  | Numeric | Years |  | The length or duration of a service life. The lower bound indicates pessimistic service life, the upper bound indicates optimistic service life, and the setpoint indicates the typical service life.
| Service Life Factors |  |  |  | Text |  |  | Captures various factors that impact the expected service life of elements within the system or zone.
| Design Level |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of design level employed.
| Indoor Environment |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the indoor environment (where appropriate).
| In Use Conditions |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the conditions in which components are operating.
| Maintenance Level |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the level or degree of maintenance applied to components.
| Outdoor Environment |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the outdoor environment (where appropriate)
| Quality Of Components |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the quality of components used.
| Work Execution Level |  |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the quality of work executed.
| Warranty | [6 empty] | An assurance given by the seller or provider of an artefact that the artefact is without defects and will operate as described for a defined period of time without failure and that if a defect does arise during that time, that it will be corrected by the seller or provider.
| Exclusions |  |  |  | Text |  |  | Items, conditions or actions that may be excluded from the warranty or that may cause the warranty to become void.
| Is Extended Warranty |  |  |  | Logic |  | True or False | Indication of whether this is an extended warranty whose duration is greater than that normally assigned to an artefact (=TRUE) or not (= FALSE).
| Point Of Contact |  |  |  | Text |  |  | The organization that should be contacted for action under the terms of the warranty.
| Warranty Content |  |  |  | Text |  |  | The content of the warranty.
| Warranty End Date |  |  |  | Numeric | Date |  | The date on which the warranty expires.
| Warranty Identifier |  |  |  | Text |  |  | The identifier assigned to a warranty.
| Warranty Period |  |  |  | Numeric | Years |  | The time duration during which a manufacturer or supplier guarantees or warrants the performance of an artefact.
| Warranty Start Date |  |  |  | Numeric | Date |  | The date on which the warranty commences.
Item-Specific Attributes
|  | Air Terminal Box | [5 empty] | an air terminal box typically participates in an HVAC duct distribution system and is used to control or modulate the amount of air delivered to its downstream ductwork
|  |  | Airflow Rate Range |  | Numeric | Cubic Feet/Minute |  | Range of airflow that can be delivered. |  | x | x | x | x
|  |  | Air Pressure Range |  | Numeric | Cubic Feet/Minute |  | Allowable air static pressure range at the entrance of the air terminal box. |  | x | x | x | x
|  |  | Arrangement Type |  | Text |  | Single Duct, Dual Duct | Terminal box arrangement. Single Duct: Terminal box receives warm or cold air from a single air supply duct. Dual Duct: Terminal box receives warm and cold air from separate air supply ducts. |  |  | x | x | x
|  |  | Has Fan |  | Text |  | True or False | Terminal box has a fan inside (fan powered box). |  | x | x | x | x
|  |  | Has Return Air |  | Logic |  | True or False | Terminal box has return air mixed with supply air from duct work. |  | x | x | x | x
|  |  | Has Sound Attenuator |  | Logic |  | True or False | Terminal box has a sound attenuator. |  | x | x | x | x
|  |  | Housing Thickness |  | Logic | Inches |  | Air terminal box housing material thickness. |  |  |  | x | x
|  |  | Nominal Air Flow Rate |  | Numeric | Cubic Feet/Minute |  | Nominal airflow rate. |  | x | x | x | x
|  |  | Nominal Damper Diameter |  | Numeric | Inches |  | Nominal damper diameter. |  | x | x | x | x
|  |  | Nominal Inlet Air Pressure |  | Numeric | PSI |  | Nominal airflow inlet static pressure. |  | x | x | x | x
|  |  | Operation Temperature Range |  | Numeric | Degree F |  | Allowable operational range of the ambient air temperature. |  | x | x | x | x
|  |  | Reheat Type |  | Text |  |  | Terminal box reheat type. |  | x | x | x | x
|  |  | Return Air Fraction Range |  | Numeric | None |  | Allowable return air fraction range as a fraction of discharge airflow. |  | x | x | x | x
|  |  | Airflow Curve |  | Numeric | Cubic Feet/Minute |  | Air flowrate versus damper position relationship; airflow = f ( valve position).
|  |  | Atmospheric Pressure |  | Numeric | PSI |  | Ambient atmospheric pressure.
|  |  | Damper Position |  | Numeric | None | 1,2,3… | Control damper position, ranging from 0 to 1.
|  |  | Sound Rating |  | Numeric | dB |  | Sound performance.
|  | Air Terminal | [5 empty] | An air terminal is a terminating or origination point for the transfer of air between distribution system(s) and one or more spaces. It can also be used for the transfer of air between adjacent spaces.
|  |  | Air Diffusion Performance Index |  | Numeric | None |  | The Air Diffusion Performance Index (ADPI) is used for cooling mode conditions. If several measurements of air velocity and air temperature are made throughout the occupied zone of a space, the ADPI is the percentage of locations where measurements were taken that meet the specifications for effective draft temperature and air velocity. |  | x | x | x | x
|  |  | Airflow Rate Range |  | Numeric | Cubic Feet/Minute |  | Air flowrate range within which the air terminal is designed to operate. |  | x | x | x | x
|  |  | Air Flowrate Versus Flow Control Element |  | Numeric | Cubic Feet/Minute |  | Air flowrate versus flow control element position at nominal pressure drop. |  |  | x | x | x
|  |  | Core Set Horizontal |  | Numeric | Degrees |  | Degree of horizontal (in the X-axis of the Local Placement) blade set from the centerline. |  |  | x | x | x
|  |  | Core Set Vertical |  | Numeric | Degrees |  | Degree of vertical (in the Y-axis of the Local Placement) blade set from the centerline. |  |  | x | x | x
|  |  | Core Type |  | Text |  |  | Identifies the way the core of the Air Terminal is constructed. |  |  | x | x | x
|  |  | Discharge Direction |  | Text |  | Parallel, Perpendicular, Adjustable | Discharge direction of the air terminal. Parallel: discharges parallel to mounting surface designed so that flow attaches to the surface. Perpendicular: discharges away from mounting surface. Adjustable: both parallel and perpendicular discharge. |  | x | x | x | x
|  |  | Effective Area |  | Numeric | Square Feet |  | Effective discharge area of the air terminal. |  | x | x | x | x
|  |  | Face Type |  | Text |  |  | Identifies how the terminal face of an Air Terminal is constructed. |  |  | x | x | x
|  |  | Finish Color |  | Text |  |  | The finish color for the air terminal. |  |  | x | x | x
|  |  | Finish Type |  | Text |  |  | The type of finish for the air terminal. |  |  | x | x | x
|  |  | Flow Control Type |  | Text |  |  | Type of flow control element that may be included as a part of the construction of the air terminal. |  |  | x | x | x
|  |  | Flow Pattern |  | Text |  |  | Flow pattern. |  | x | x | x | x
|  |  | Has Integral Control |  | Logic |  | True or False | If TRUE, a self powered temperature control is included in the Air Terminal. |  |  | x | x | x
|  |  | Has Sound Attenuator |  | Logic |  | True or False | If TRUE, the air terminal has sound attenuation. |  |  | x | x | x
|  |  | Has Thermal Insulation |  | Logic |  | True or False | If TRUE, the air terminal has thermal insulation. |  |  | x | x | x
|  |  | Mounting Type |  | Text |  | Surface, Flat flush, Lay-in | The way the air terminal is mounted to the ceiling, wall, etc. |  | x | x | x | x
|  |  | Neck Area |  | Numeric | Square Inches |  | Neck area of the air terminal. |  |  | x | x | x
|  |  | Number Of Slots |  | Numeric | None | 1,2,3… | Number of slots. |  |  | x | x | x
|  |  | Shape |  | Text |  |  | Shape of the air terminal. Slot is typically a long narrow supply device with an aspect ratio generally greater than 10 to 1. |  | x | x | x | x
|  |  | Slot Length |  | Numeric | Inches |  | Slot length. |  | x | x | x | x
|  |  | Slot Width |  | Numeric | Inches |  | Slot width. |  | x | x | x | x
|  |  | Temperature Range |  | Numeric | Degree F |  | Temperature range within which the air terminal is designed to operate. |  |  | x | x | x
|  |  | Throw Length |  | Numeric | Inches |  | The horizontal or vertical axial distance an airstream travels after leaving an Air Terminal before the maximum stream velocity is reduced to a specified terminal velocity under isothermal conditions at the upper value of the Air Flow rate Range. |  |  |  | x | x
|  |  | Air Flow Rate |  | Numeric | Cubic Feet/Minute |  | Volumetric flow rate.
|  |  | Centerline Air Velocity |  | Numeric | Feet/Minute |  | Centerline air velocity versus distance from the diffuser and temperature differential
|  |  | Induction Ratio |  | Numeric | None |  | Induction ratio versus distance from the diffuser and its discharge direction; induction ratio (or entrainment ratio) is the ratio of the volumetric flow rate in the jet to the volumetric flow rate at the air terminal.
|  |  | Neck Air Velocity |  | Numeric | Feet/Minute |  | Air velocity at the neck.
|  |  | Pressure Drop |  | Numeric | Inches of Water |  | Drop in total pressure between inlet and outlet at nominal air-flow rate.
|  |  | Supply Air Temperature Cooling |  | Numeric | Degree F |  | Supply air temperature in cooling mode.
|  |  | Supply Air Temperature Heating |  | Numeric | Degree F |  | Supply air temperature in heating mode.
|  |  | Air Flow Rate |  | Numeric | Cubic Feet/Minute |  | The actual airflow rate as designed.
|  |  | Airflow Type |  | Text |  |  | Enumeration defining the functional type of air flow through the terminal.
|  |  | Location |  | Text |  |  | Location (a single type of diffuser can be used for multiple locations); high means close to ceiling.
|  | Air to Air Heat Exchanger | [5 empty] | An air-to-air heat recovery device employs a counter-flow heat exchanger between inbound and outbound air flow.
|  |  | Has Defrost |  | Logic |  | True or False | The heat exchanger has defrost function or not. |  |  | x | x | x
|  |  | Heat Transfer Type |  | Text |  |  | Type of heat transfer between the two air streams. |  | x | x | x | x
|  |  | Operational Temperature Range |  | Numeric | Degree F |  | Allowable operation ambient air temperature range. |  | x | x | x | x
|  |  | Primary Airflow Rate Range |  | Numeric | Cubic Feet/Minute |  | possible range of primary airflow that can be delivered.. |  | x | x | x | x
|  |  | Secondary Airflow Rate Range |  | Numeric | Cubic Feet/Minute |  | possible range of secondary airflow that can be delivered. |  | x | x | x | x
|  |  | Air Pressure Drop Curves |  | Numeric | PSI |  | Air pressure drop as function of air flow rate.
|  |  | Defrost Temperature Effectiveness |  | Numeric | Degree F |  | Temperature heat transfer effectiveness when defrosting is active.
|  |  | Humidity Effectiveness |  | Numeric | None |  | Humidity heat transfer effectiveness: The ratio of primary airflow absolute humidity changes to maximum possible absolute humidity changes.
|  |  | Latent Heat Transfer Rate |  | Numeric | BTU/Ft2·◦F |  | Latent heat transfer rate.
|  |  | Sensible Effectiveness |  | Numeric | None |  | Sensible heat transfer effectiveness, where effectiveness is defined as the ratio of heat transfer to maximum possible heat transfer.
|  |  | Sensible Effectiveness Table |  | Numeric | None |  | Sensible heat transfer effectiveness curve as a function of the primary and secondary air flow rate.
|  |  | Sensible Heat Transfer Rate |  | Numeric | BTU/Ft2·◦F |  | Sensible heat transfer rate.
|  |  | Temperature Effectiveness |  | Numeric | None |  | Temperature heat transfer effectiveness: The ratio of primary airflow temperature changes to maximum possible temperature changes.
|  |  | Total Effectiveness |  | Numeric | None |  | Total heat transfer effectiveness: The ratio of heat transfer to the maximum possible heat transfer.
|  |  | Total Effectiveness Table |  | Numeric | None |  | Total heat transfer effectiveness curve as a function of the primary and secondary air flow rate.
|  |  | Total Heat Transfer Rate |  | Numeric | BTU/Ft2·◦F |  | Total heat transfer rate.
|  | Boiler | [5 empty] | A boiler is a closed, pressure-rated vessel in which water or other fluid is heated using an energy source such as natural gas, heating oil, or electricity. The fluid in the vessel is then circulated out of the boiler for use in various processes or heating applications.
|  |  | Energy Source |  | Text |  |  | Enumeration defining the energy source or fuel combusted to generate heat. |  | x | x | x | x
|  |  | Heat Transfer Surface Area |  | Numeric | Square Feet |  | Total heat transfer area of the vessel. |  | x | x | x | x
|  |  | Is Water Storage Heater |  | Logic |  | True or False | This is used to identify if the boiler has storage capacity (TRUE). If FALSE, then there is no storage capacity built into the boiler, such as an instantaneous hot water heater. |  | x | x | x | x
|  |  | Nominal Energy Consumption |  | Numeric | BTU |  | Nominal fuel consumption rate required to produce the total boiler heat output. |  | x | x | x | x
|  |  | Nominal Part Load Ratio |  | Numeric | None |  | Allowable part load ratio range. |  | x | x | x | x
|  |  | Operating Mode |  | Text |  |  | Identifies the operating mode of the boiler. |  | x | x | x | x
|  |  | Outlet Temperature Range |  | Numeric | Degree F |  | Allowable outlet temperature of either the water or the steam. |  | x | x | x | x
|  |  | Partial Load Efficiency Curves |  | Numeric | Percent |  | Boiler efficiency as a function of the partial load factor; E = f (partial Load factor). |  | x | x | x | x
|  |  | Pressure Rating |  | Numeric | PSI |  | Nominal pressure rating of the boiler as rated by the agency having jurisdiction. |  | x | x | x | x
|  |  | Water Inlet Temperature Range |  | Numeric | Degree F |  | Allowable water inlet temperature range. |  | x | x | x | x
|  |  | Water Storage Capacity |  | Numeric | Gallons |  | Water storage capacity. |  | x | x | x | x
|  |  | Auxiliary Energy Consumption |  | Text |  |  | Boiler secondary energy source consumption pumps).
|  |  | Combustion Efficiency |  | Numeric | Percent |  | Combustion efficiency under nominal condition.
|  |  | Combustion Temperature |  | Numeric | Degree F |  | Average combustion chamber temperature.
|  |  | Energy Source Consumption |  | Numeric | BTU/Hr |  | Energy consumption.
|  |  | Load Real |  | Numeric | BTU |  | Boiler real load.
|  |  | Operational Efficiency |  | Numeric | Percent |  | Operational efficiency: boiler output divided by total energy input (electrical and fuel).
|  |  | Part Load Ratio |  | Numeric | None |  | Ratio of the real to the nominal capacity.
|  |  | Primary Energy Consumption |  | Numeric | BTU/Hr |  | Boiler primary energy source consumption (i.e., the fuel consumed for changing the thermodynamic state of the fluid).
|  |  | Working Pressure |  | Numeric | PSI |  | Boiler working pressure.
|  |  | Steam Boiler |  | Text |  |  | Steam boiler type Specific Baseline Attributes.
|  |  |  | Heat Output | Numeric | BTU/Hr |  | Total nominal heat output as listed by the Boiler manufacturer. For steam boilers, it is a function of inlet temperature versus steam pressure. |  | x | x | x | x
|  |  |  | Maximum Outlet Pressure | Numeric | PSI |  | Maximum steam outlet pressure. |  | x | x | x | x
|  |  |  | Nominal Efficiency | Numeric | Percent |  | The nominal efficiency of the boiler as defined by the manufacturer. For steam boilers, a function of inlet temperature versus steam pressure. |  | x | x | x | x
|  |  | Water Boiler |  | Text |  |  | Water boiler type Specific Baseline Attributes.
|  |  |  | Heat Output | Numeric | BTU/Hr |  | Total nominal heat output as listed by the Boiler manufacturer. For water boilers, it is a function of inlet versus outlet temperature. For steam boilers, it is a function of inlet temperature versus steam pressure |  | x | x | x | x
|  |  |  | Nominal Efficiency | Numeric | Percent |  | The nominal efficiency of the boiler as defined by the manufacturer. For water boilers, a function of inlet versus outlet temperature. |  | x | x | x | x
|  | Chiller | [5 empty] | A chiller is a device used to remove heat from a liquid via a vapor-compression or absorption refrigeration cycle to cool a fluid, typically water or a mixture of water and glycol. The chilled fluid is then used to cool and dehumidify air in a building.
|  |  | Capacity Curve |  | Numeric | None |  | Chiller cooling capacity is a function of condensing temperature and evaporating temperature. |  | x | x | x | x
|  |  | Coefficient Of Performance Curve |  | Numeric | None |  | Chiller coefficient of performance (COP) is function of condensing temperature and evaporating temperature. |  | x | x | x | x
|  |  | Full Load Ratio Curve |  | Numeric | None |  | Ratio of actual power to full load power as a quadratic function of part load |  | x | x | x | x
|  |  | Nominal Capacity |  | Numeric | Ton |  | Nominal cooling capacity of chiller at standardized conditions as defined by the agency having jurisdiction. |  | x | x | x | x
|  |  | Nominal Condensing Temperature |  | Numeric | Degree F |  | Chiller condensing temperature. |  | x | x | x | x
|  |  | Nominal Efficiency |  | Numeric | Percent |  | Nominal chiller efficiency under nominal conditions. |  | x | x | x | x
|  |  | Nominal Evaporating Temperature |  | Numeric | Degree F |  | Chiller evaporating temperature. |  | x | x | x | x
|  |  | Nominal Heat Rejection Rate |  | Numeric | BTU/Hr |  | Sum of the refrigeration effect and the heat equivalent of the power input to the compressor. |  | x | x | x | x
|  |  | Nominal Power Consumption |  | Numeric | Horsepower |  | Nominal total power consumption. |  | x | x | x | x
|  |  | Capacity |  | Numeric | Ton |  | The product of the ideal capacity and the overall volumetric efficiency of the compressor. |  | x | x | x | x
|  |  | Coefficient Of Performance |  | Numeric | None |  | The Coefficient of performance (COP) is the ratio of heat removed to energy input. |  | x | x | x | x
|  |  | Energy Efficiency Ratio |  | Numeric | BTU/Hr/Watt |  | The Energy efficiency ratio (EER) is the ratio of net cooling capacity to the total input rate of electric power applied |  | x | x | x | x
|  | Coil | [5 empty] | A coil is a device used to provide heat transfer between non-mixing media.
|  |  | Airflow Rate Range |  | Numeric | Cubic Feet/Minute | For cases where there is no airflow across the coil (e.g. electric coil in a floor slab), then the value is zero. | Possible range of airflow that can be delivered. |  | x | x | x | x
|  |  | Nominal Latent Capacity |  | Numeric | BTU |  | Nominal latent capacity. |  | x | x | x | x
|  |  | Nominal Sensible Capacity |  | Numeric | BTU |  | Nominal sensible capacity. |  | x | x | x | x
|  |  | Nominal U A |  | Numeric | None |  | Nominal UA value. |  | x | x | x | x
|  |  | Operational Temperature Range |  | Numeric | Degree F |  | Allowable operational air temperature range. |  | x | x | x | x
|  |  | Placement Type |  | Text |  | Floor, Ceiling, Unit | Indicates the placement of the coil |  | x | x | x | x
|  |  | Air Pressure Drop Curve |  | Numeric | PSI |  | Air pressure drop curve, pressure drop – flow rate curve
|  |  | Atmospheric Pressure |  | Numeric | PSI |  | Ambient atmospheric pressure.
|  |  | Face Velocity |  | Numeric | Feet/Minute |  | Air velocity through the coil.
|  |  | Sound Curve |  | Numeric | Decibel |  | Regenerated sound versus air-flow rate.
|  |  | Sound Attenuation |  | Logic |  | True or False | TRUE if the coil has sound attenuation, FALSE if it does not.
|  |  | Water Coil |  | Text |  |  | Hydronic coil type attributes.
|  |  | Bypass Factor |  | Numeric | None | between 0-1 | Fraction of air that is bypassed by the coil .
|  |  | Coil Connection Direction |  | Text |  |  | Coil connection direction (facing into the air stream).
|  |  | Coil Coolant |  | Text |  |  | The fluid used for heating or cooling used by the hydronic coil.
|  |  | Coil Face Area |  | Numeric | Square Inches |  | Coil face area in the direction against air the flow.
|  |  | Coil Fluid Arrangement |  | Text |  | Cross Counter Flow, Crossflow, Cross Parallel Flow | Fluid flow arrangement of the coil
|  |  | Fluid |  | Text |  |  | The properties of the hydronic fluid used for heat transfer within the coil tubes.
|  |  | Fluid Pressure Range |  | Numeric | PSI |  | Allowable water working pressure range inside the tube.
|  |  | Heat Exchange Surface Area |  | Numeric | Square Feet |  | Heat exchange surface area associated with U-value.
|  |  | Primary Surface Area |  | Numeric | Square Feet |  | Primary heat transfer surface area of the tubes and headers.
|  |  | Secondary Surface Area |  | Numeric | Square Feet |  | Secondary heat transfer surface area created by fins.
|  |  | Sensible Heat Ratio |  | Numeric | None |  | Air-side sensible heat ratio, or fraction of sensible heat transfer to the total heat transfer.
|  |  | Total U A Curves |  | Numeric | None |  | Total UA curves, UA - air and water velocities
|  |  | Water Pressure Drop Curve |  | Numeric | PSI |  | Water pressure drop curve, pressure drop – flow rate curve
|  |  | Wet Coil Fraction |  | Numeric | None | between 0-1 | Fraction of coil surface area that is wet (0-1).
|  | Compressor | [5 empty] | A compressor is a device that compresses a fluid typically used in a refrigeration circuit.
|  |  | Compressor Speed |  | Numeric | RPM |  | Compressor speed. |  | x | x | x | x
|  |  | Has Hot Gas Bypass |  | Logic |  | True or False | Whether or not hot gas bypass is provided for the compressor |  | x | x | x | x
|  |  | Ideal Capacity |  | Numeric | Tonnage |  | Compressor capacity under ideal conditions. |  | x | x | x | x
|  |  | Ideal Shaft Power |  | Numeric | Horsepower |  | Compressor shaft power under ideal conditions. |  | x | x | x | x
|  |  | Impeller Diameter |  | Numeric | Inches |  | Diameter of compressor impeller - used to scale performance of geometrically similar compressors. |  | x | x | x | x
|  |  | Maximum Part Load Ratio |  | Numeric | None |  | Maximum part load ratio as a fraction of nominal capacity. |  | x | x | x | x
|  |  | Minimum Part Load Ratio |  | Numeric | None |  | Minimum part load ratio as a fraction of nominal capacity. |  | x | x | x | x
|  |  | Nominal Capacity |  | Numeric | Tonnage |  | Compressor nameplate capacity. |  | x | x | x | x
|  |  | Power Source |  | Text |  |  | Type of power driving the compressor. |  | x | x | x | x
|  |  | Refrigerant Class |  | Text |  | CFC, HCFC, HFC | Refrigerant class used by the compressor. |  | x | x | x | x
|  |  | Refrigerant Type |  | Text |  |  | Refrigerant material. |  | x | x | x | x
|  |  | Coefficient Of Performance |  | Numeric | None |  | Coefficient of performance (COP).
|  |  | Compression Efficiency |  | Numeric | Percent |  | Ratio of the work required for isentropic compression of the gas to the work delivered to the gas within the compression volume
|  |  | Compressor Capacity |  | Numeric | Tonnage |  | The product of the ideal capacity and the overall volumetric efficiency of the compressor.
|  |  | Compressor Total Efficiency |  | Numeric | Percent |  | Ratio of the thermal cooling capacity to electrical input.
|  |  | Compressor Total Heat Gain |  | Numeric | BTU/Hr |  | Compressor total heat gain.
|  |  | Energy Efficiency Ratio |  | Numeric | None |  | Energy efficiency ratio (EER).
|  |  | Friction Heat Gain |  | Numeric | BTU/Hr |  | Friction heat gain.
|  |  | Full Load Ratio |  | Numeric | None |  | Ratio of actual power to full load power as a quadratic function of part load, at certain condensing and evaporating temperature
|  |  | Input Power |  | Numeric | HP |  | Input power to the compressor motor.
|  |  | Isentropic Efficiency |  | Numeric | Percent |  | Ratio of the work required for isentropic compression of the gas to work input to the compressor shaft.
|  |  | Lubricant Pump Heat Gain |  | Numeric | BTU/Hr |  | Lubricant pump heat gain.
|  |  | Mechanical Efficiency |  | Numeric | Percent |  | Ratio of the work (as measured) delivered to the gas to the work input to the compressor shaft.
|  |  | Shaft Power |  | Numeric | HP |  | The actual shaft power input to the compressor.
|  |  | Volumetric Efficiency |  | Numeric | Percent |  | Ratio of the actual volume of gas entering the compressor to the theoretical displacement of the compressor.
|  | Condenser | [5 empty] | A condenser is a device that is used to dissipate heat, typically by condensing a substance such as a refrigerant from its gaseous to its liquid state.
|  |  | External Surface Area |  | Numeric | Square Feet |  | External surface area (both primary and secondary area). |  | x | x | x | x
|  |  | Internal Refrigerant Volume |  | Numeric | Cubic Inch |  | Internal volume of condenser (refrigerant side). |  | x | x | x | x
|  |  | Internal Surface Area |  | Numeric | Square Feet |  | Internal surface area. |  | x | x | x | x
|  |  | Internal Water Volume |  | Numeric | Gallons |  | Internal volume of condenser (water side). |  | x | x | x | x
|  |  | Nominal Heat Transfer Area |  | Numeric | Square Feet |  | Nominal heat transfer surface area associated with nominal overall heat transfer coefficient. |  | x | x | x | x
|  |  | Nominal Heat Transfer Coefficient |  | Numeric | None |  | Nominal overall heat transfer coefficient associated with nominal heat transfer area. |  | x | x | x | x
|  |  | Refrigerant Class |  | Text |  | CFC, HCFC, HFC | Refrigerant class used by the condenser. |  | x | x | x | x
|  |  | Refrigerant Material |  | Text |  |  | The refrigerant material used for heat transfer purposes. |  | x | x | x | x
|  |  | Compressor Condenser Heat Gain |  | Numeric | BTU |  | Heat gain between condenser inlet to compressor outlet.
|  |  | Compressor Condenser Pressure Drop |  | Numeric | PSI |  | Pressure drop between condenser inlet and compressor outlet.
|  |  | Condenser Mean Void Fraction |  | Numeric | None |  | Mean void fraction in condenser.
|  |  | Condensing Temperature |  | Numeric | Degree F |  | Refrigerant condensing temperature.
|  |  | Exterior Heat Transfer Coefficient |  | Numeric | None |  | Exterior heat transfer coefficient associated with exterior surface area.
|  |  | Heat Rejection Rate |  | Numeric | BTU/Hr |  | Sum of the refrigeration effect and the heat equivalent of the power input to the compressor.
|  |  | Interior Heat Transfer Coefficient |  | Numeric | None |  | Interior heat transfer coefficient associated with interior surface area.
|  |  | Logarithmic Mean Temperature Difference |  | Numeric | Degree F |  | Logarithmic mean temperature difference between refrigerant and water or air.
|  |  | Refrigerant Fouling Resistance |  | Numeric | None |  | Fouling resistance on the refrigerant side.
|  |  | U A curves |  | Numeric | None |  | UV = f (VExterior, VInterior), UV as a function of interior and exterior fluid flow velocity at the entrance.
|  |  | Water Fouling Resistance |  | Numeric | Hr x Ft2 °F/BTU |  | Fouling resistance on water/air side.
|  | Chilled Beam | [5 empty] | A cooled beam (or chilled beam) is a device typically used to cool air by circulating a fluid such as chilled water through exposed finned tubes above a space
|  |  | Coil Length |  | Numeric | Feet |  | Length of coil. |  |  | x | x | x
|  |  | Coil Width |  | Numeric | Inches |  | Width of coil. |  |  | x | x | x
|  |  | Finish Color |  | Text |  |  | Finish color for cooled beam. |  |  | x | x | x
|  |  | Integrated Lighting Type |  | Text |  |  | Integrated lighting in cooled beam. |  | x | x | x | x
|  |  | Is Free Hanging |  | Logic |  | True or False | Is it free hanging type (not mounted in a false ceiling)? |  | x | x | x | x
|  |  | Nominal Cooling Capacity |  | Numeric | BTU/Lineal Feet |  | Nominal cooling capacity. |  | x | x | x | x
|  |  | Nominal Heating Capacity |  | Numeric | BTU/Lineal Feet |  | Nominal heating capacity. |  | x | x | x | x
|  |  | Nominal Return Water Temperature Cooling |  | Numeric | Degree F |  | Nominal return water temperature (refers to nominal cooling capacity). |  | x | x | x | x
|  |  | Nominal Return Water Temperature Heating |  | Numeric | Degree F |  | Nominal return water temperature (refers to nominal heating capacity). |  | x | x | x | x
|  |  | Nominal Supply Water Temperature Cooling |  | Numeric | Degree F |  | Nominal supply water temperature (refers to nominal cooling capacity). |  | x | x | x | x
|  |  | Nominal Supply Water Temperature Heating |  | Numeric | Degree F |  | Nominal supply water temperature (refers to nominal heating capacity). |  | x | x | x | x
|  |  | Nominal Surrounding Humidity Cooling |  | Numeric | Percent |  | Nominal surrounding humidity (refers to nominal cooling capacity). |  | x | x | x | x
|  |  | Nominal Surrounding Temperature Cooling |  | Numeric | Degree F |  | Nominal surrounding temperature (refers to nominal cooling capacity). |  | x | x | x | x
|  |  | Nominal Surrounding Temperature Heating |  | Numeric | Degree F |  | Nominal surrounding temperature (refers to nominal heating capacity). |  | x | x | x | x
|  |  | Nominal Water Flow Cooling |  | Numeric | Gallons/Minute |  | Nominal water flow (refers to nominal cooling capacity). |  | x | x | x | x
|  |  | Nominal Water Flow Heating |  | Numeric | Gallons/Minute |  | Nominal water flow (refers to nominal heating capacity). |  | x | x | x | x
|  |  | Pipe Connection |  | Text |  |  | The manner in which the pipe connection is made to the cooled beam. |  | x | x | x | x
|  |  | Water Flow Control System Type |  | Text |  |  | Factory fitted water flow control system. |  | x | x | x | x
|  |  | Active Chilled Beam Configuration |  | Text |  |  | Active (ventilated) cooled beam
|  |  | Air Flow Configuration |  | Text |  |  | Air flow configuration type of cooled beam.
|  |  | Air Flow Rate |  | Numeric | CFM/Lineal Feet |  | Air flow rate.
|  |  | Air Pressure Drop Curves |  | Numeric | Inches of Water |  | Air pressure drop as function of air flow rate.
|  |  | Airflow Rate Range |  | Numeric | CFM/Lineal Feet |  | Possible range of airflow that can be delivered.
|  |  | Beam Cooling Capacity |  | Numeric | BTU/Lineal Feet |  | Cooling capacity of beam. This excludes cooling capacity of supply air.
|  |  | Beam Heating Capacity |  | Numeric | BTU/Lineal Feet |  | Heating capacity of beam. This excludes heating capacity of supply air.
|  |  | Connection Size |  | Numeric | Inches |  | Duct connection diameter.
|  |  | Cooling Water Flow Rate |  | Numeric | Gallons/Minute |  | Water flow rate for cooling.
|  |  | Correction Factor For Cooling |  | Numeric | None |  | Correction factor k as a function of water flow rate (used to calculate cooling capacity).
|  |  | Correction Factor For Heating |  | Numeric | None |  | Correction factor k as a function of water flow rate (used to calculate heating capacity).
|  |  | Heating Water Flow Rate |  | Numeric | Gallons/Minute |  | Water flow rate for heating.
|  |  | Return Water Temperature Cooling |  | Numeric | Degree F |  | Return water temperature in cooling mode.
|  |  | Return Water Temperature Heating |  | Numeric | Degree F |  | Return water temperature in heating mode.
|  |  | Supply Air Connection Type |  | Text |  |  | The manner in which the pipe connection is made to the cooled beam.
|  |  | Supply Water Temperature Cooling |  | Numeric | Degree F |  | Supply water temperature in cooling mode.
|  |  | Supply Water Temperature Heating |  | Numeric | Degree F |  | Supply water temperature in heating mode.
|  |  | Throw |  | Numeric | Feet |  | Distance cooled beam throws the air.
|  |  | Total Cooling Capacity |  | Numeric | BTU/Lineal Feet |  | Total cooling capacity. This includes cooling capacity of beam and cooling capacity of supply air.
|  |  | Total Heating Capacity |  | Numeric | BTU/Lineal Feet |  | Total heating capacity. This includes heating capacity of beam and heating capacity of supply air.
|  |  | Water Pressure Drop Curves |  | Numeric | Inches of Water |  | Water pressure drop as function of water flow rate.
|  | Cooling Tower | [5 empty] | A cooling tower is a device which rejects heat to ambient air by circulating a fluid such as water through it to reduce its temperature by partial evaporation.
|  |  | Ambient Design Dry Bulb Temperature |  | Numeric | Degree F |  | Ambient design dry bulb temperature used for selecting the cooling tower. |  | x | x | x | x
|  |  | Ambient Design Wet Bulb Temperature |  | Numeric | Degree F |  | Ambient design wet bulb temperature used for selecting the cooling tower. |  | x | x | x | x
|  |  | Basin Reserve Volume |  | Numeric | Gallons |  | Volume between operating and overflow levels in cooling tower basin. |  | x | x | x | x
|  |  | Capacity Control |  | Text |  | Fan Cycling, Two Speed Fan, Variable Speed Fan, Dampers Control, Bypass Valve Control, Multiple Series Pumps, Two Speed Pump, Variable Speed Pump | Fan Cycling: Fan is cycled on and off to control duty. Two Speed Fan: Fan is switched between low and high speed to control duty. Variable Speed Fan: Fan speed is varied to control duty. Dampers Control: Dampers modulate the air flow to control duty. Bypass Valve Control: Bypass valve modulates the water flow to control duty. Multiple Series Pumps: Turn on/off multiple series pump to control duty. Two Speed Pump: Switch between high/low pump speed to control duty. Variable Speed Pump: vary pump speed to control duty. |  | x | x | x | x
|  |  | Circuit Type |  | Text |  | Open Circuit ; Close Circuit ; Wet; Dry; Dry Wet; | Open Circuit: Exposes water directly to the cooling atmosphere. Close Circuit: The fluid is separated from the atmosphere by a heat exchanger. Wet: The air stream or the heat exchange surface is evaporatively cooled. Dry: No evaporation into the air stream. Dry Wet: A combination of a dry tower and a wet tower. |  | x | x | x | x
|  |  | Control Strategy |  | Text |  | Fixed Exiting Water Temp, Wet Bulb Temp Reset | Fixed Exiting Water Temp: The capacity is controlled to maintain a fixed exiting water temperature. Wet Bulb Temp Reset: The set-point is reset based on the wet-bulb temperature. |  | x | x | x | x
|  |  | Flow Arrangement |  | Text |  | Counter Flow, Crossflow, Parallel Flow | Counter Flow: Air and water flow enter in different directions. Crossflow: Air and water flow are perpendicular. Parallel Flow: air and water flow enter in same directions. |  | x | x | x | x
|  |  | Lift Elevation Difference |  | Numeric | Feet |  | Elevation difference between cooling tower sump and the top of the tower. |  | x | x | x | x
|  |  | Nominal Capacity |  | Numeric | Tonnage |  | Nominal cooling tower capacity in terms of heat transfer rate of the cooling tower between air stream and water stream at nominal conditions. |  | x | x | x | x
|  |  | Number Of Cells |  | Numeric | None |  | Number of cells in one cooling tower unit. |  | x | x | x | x
|  |  | Operation Temperature Range |  | Numeric | Degree F |  | Allowable operation ambient air temperature range. |  | x | x | x | x
|  |  | Spray Type |  | Text |  | Spray Filled, Splash Type Fill, Film Type Fill | Water Spray Fill Type |  | x | x | x | x
|  |  | Water Requirement |  | Numeric | Gallons/Minute |  | Make-up water requirements. |  | x | x | x | x
|  |  | Capacity |  | Numeric | Tonnage |  | Cooling tower capacity in terms of heat transfer rate of the cooling tower between air stream and water stream.
|  |  | Heat Transfer Coefficient |  | Numeric | None |  | Heat transfer coefficient-area product.
|  |  | Sump Heater Power |  | Numeric | Watts |  | Electrical heat power of sump heater.
|  |  | U A Curve |  | Numeric | None |  | UA value as a function of fan speed at certain water flow rate, UA = f ( fan speed).
|  |  | Water Delta |  | Numeric | Degree F |  | Water temperature change as a function of wet-bulb temperature, water entering temperature, water flow rate, air flow rate, Tdiff = f ( Twet-bulb, Twater,in, water, mair).
|  | Damper | [5 empty] | A damper typically participates in an HVAC duct distribution system and is used to control or modulate the flow of air.
|  |  | Blade Action |  | Text |  |  | Blade action. |  | x | x | x | x
|  |  | Blade Edge |  | Text |  |  | Blade edge. |  | x | x | x | x
|  |  | Blade Material |  | Text |  |  | The material from which the damper blades are constructed. |  |  | x | x | x
|  |  | Blade Shape |  | Text |  |  | Blade shape. Flat means triple V-groove. |  |  | x | x | x
|  |  | Blade Thickness |  | Numeric | Inches |  | The thickness of the damper blade. |  |  | x | x | x
|  |  | Close Off Rating |  | Text |  |  | Close off rating. |  | x | x | x | x
|  |  | Face Area |  | Numeric | Square Inches |  | Face area open to the airstream. |  |  | x | x | x
|  |  | Frame Depth |  | Numeric | Inches |  | The length (or depth) of the damper frame. |  |  | x | x | x
|  |  | Frame Material |  | Text |  |  | The material from which the damper frame is constructed. |  |  | x | x | x
|  |  | Frame Thickness |  | Numeric | Inches |  | The thickness of the damper frame material. |  |  | x | x | x
|  |  | Frame Type |  | Text |  | Standard, Single Flange, Single Reversed Flange, Double Flange, User Defined | The type of frame used by the damper |  |  | x | x | x
|  |  | Leakage Curve |  | Numeric | None |  | Leakage versus pressure drop; Leakage = f (pressure). |  | x | x | x | x
|  |  | Leakage Fully Closed |  | Numeric | CFM/Ft2 |  | Leakage when fully closed. |  | x | x | x | x
|  |  | Loss Coefficient Curve |  | Numeric | None |  | Loss coefficient – blade position angle curve; ratio of pressure drop to velocity pressure versus blade angle; C = f (blade angle position). |  | x | x | x | x
|  |  | Maximum Air Flow Rate |  | Numeric | Cubic Feet/Minute |  | Maximum allowable air flow rate. |  | x | x | x | x
|  |  | Maximum Working Pressure |  | Numeric | PSI |  | Maximum working pressure. |  | x | x | x | x
|  |  | Nominal Air Flow Rate |  | Numeric | Cubic Feet/Minute |  | Nominal air flow rate. |  | x | x | x | x
|  |  | Number of Blades |  | Numeric | None | 1,2,3… | Number of blades. |  |  | x | x | x
|  |  | Open Pressure Drop |  | Numeric | Inches of Water |  | Total pressure drop across damper. |  | x | x | x | x
|  |  | Operation |  | Text |  |  | The operational mechanism for the damper operation. |  | x | x | x | x
|  |  | Orientation |  | Text |  |  | The intended orientation for the damper as specified by the manufacturer. |  |  | x | x | x
|  |  | Regenerated Sound Curve |  | Numeric | Dba |  | Regenerated sound versus air flow rate. |  | x | x | x | x
|  |  | Seal Material |  | Text |  |  | The material from which the damper seals are constructed. |  |  | x | x | x
|  |  | Temperature Range |  | Numeric | Degree F |  | Temperature range. |  | x | x | x | x
|  |  | Sizing Method |  | Text |  |  | Identifies whether the damper is sized nominally or with exact measurements: NOMINAL: Nominal sizing method. EXACT: Exact sizing method.
|  |  | Air Flow Rate |  | Numeric | Cubic Feet/Minute |  | Air flow rate.
|  |  | Blade Position Angle |  | Numeric | Degrees | 0-90 | Blade position angle; angle between the blade and flow direction ( 0 - 90).
|  |  | Damper Position |  | Numeric | None | 0-1 | Damper position (0-1); damper position ( 0=closed=90deg position angle, 1=open=0deg position angle.
|  |  | Leakage |  | Numeric | CFM/Ft2 |  | Air leakage rate.
|  |  | Pressure Drop |  | Numeric | Inches of Water |  | Pressure drop.
|  |  | Pressure Loss Coefficient |  | Numeric | None |  | Pressure loss coefficient.
|  |  | Control Damper |  |  |  |  | Control damper type attributes.
|  |  |  | Control Damper Operation | Text |  |  | The inherent characteristic of the control damper operation. |  | x | x | x | x
|  |  |  | Torque Range | Numeric | Inch-Lbs |  | Torque range: minimum operational torque to maximum allowable torque. |  | x | x | x | x
|  |  | Fire Damper |  |  |  |  | Fire damper type attributes.
|  |  |  | Actuation Type | Text |  |  | Enumeration that identifies the different types of dampers. |  | x | x | x | x
|  |  |  | Enclosure Rating | Text |  |  | Enumeration that identifies the closure rating for the damper. |  | x | x | x | x
|  |  |  | Fire Resistance Rating | Text |  |  | Measure of the fire resistance rating in hours (e.g., 1.5 hours, 2 hours, etc.). |  | x | x | x | x
|  |  |  | Fusible Link Temperature | Text |  |  | The temperature that the fusible link melts. |  | x | x | x | x
|  |  | Fire Smoke Damper |  |  |  |  | Combination Fire and Smoke damper type attributes.
|  |  |  | Actuation Type | Text |  |  | Enumeration that identifies the different types of dampers. |  | x | x | x | x
|  |  |  | Enclosure Rating | Text |  |  | Enumeration that identifies the closure rating for the damper. |  | x | x | x | x
|  |  |  | Control Type | Text |  |  | The type of control used to operate the damper (e.g., Open/Closed Indicator, Resettable Temperature Sensor, Temperature Override, etc.). |  | x | x | x | x
|  |  |  | Fire Resistance Rating | Text |  |  | Measure of the fire resistance rating in hours (e.g., 1.5 hours, 2 hours, etc.). |  | x | x | x | x
|  |  |  | Fusible Link Temperature | Numeric | Degree F |  | The temperature that the fusible link melts. |  | x | x | x | x
|  |  | Smoke Damper |  |  |  |  | Smoke damper type attributes.
|  |  |  | Control Type | Text |  |  | The type of control used to operate the damper (e.g., Open/Closed Indicator, Resettable Temperature Sensor, Temperature Override, etc.) . |  | x | x | x | x
|  | Duct Silencer | [5 empty] | A duct silencer is a device that is typically installed inside a duct distribution system for the purpose of reducing the noise levels from air movement, fan noise, etc. in the adjacent space or downstream of the duct silencer device.
|  |  | Airflow Rate Range |  | Numeric | Feet/Minute |  | Possible range of airflow that can be delivered. |  | x | x | x | x
|  |  | Has Exterior Insulation |  | Logic |  | True or False | TRUE if the silencer has exterior insulation. FALSE if it does not. |  | x | x | x | x
|  |  | Hydraulic Diameter |  | Numeric | Inches |  | Hydraulic diameter. |  |  | x | x | x
|  |  | Length |  | Numeric | Inches |  | The finished length of the silencer. |  |  | x | x | x
|  |  | Temperature Range |  | Numeric | Degree F |  | Allowable minimum and maximum temperature. |  | x | x | x | x
|  |  | Weight |  | Numeric | Lbs |  | The weight of the silencer. |  | x | x | x | x
|  |  | Working Pressure Range |  | Numeric | PSI |  | Allowable minimum and maximum working pressure (relative to ambient pressure). |  | x | x | x | x
|  |  | Air Flow Rate |  | Numeric | Cubic Feet/Minute |  | Volumetric air flow rate. |  | x | x | x | x
|  |  | Air Pressure Drop Curve |  | Numeric | Inches of Water |  | Air pressure drop as a function of air flow rate. |  | x | x | x | x
|  | Engine | [5 empty] | An engine is a device that converts fuel into mechanical energy through combustion.
|  |  | Energy Source |  | Text |  |  | The source of energy. |  | x | x | x | x
|  | Evaporative Cooler | [5 empty] | An evaporative cooler is a device that cools air by saturating it with water vapor.
|  |  | Air Pressure Drop Curve |  | Numeric | Inches of Water/CFM |  | Air pressure drop as function of air flow rate. |  | x | x | x | x
|  |  | Effectiveness Table |  | Numeric | None |  | Total heat transfer effectiveness curve as a function of the primary air flow rate. |  | x | x | x | x
|  |  | Flow Arrangement |  | Text |  |  | Counter Flow: Air and water flow enter in different directions. Crossflow: Air and water flow are perpendicular. Parallel Flow: Air and water flow enter in same directions. |  |  | x | x | x
|  |  | Heat Exchange Area |  | Numeric | Square Feet |  | Heat exchange area. |  | x | x | x | x
|  |  | Operation Temperature Range |  | Numeric | Degree F |  | Allowable operation ambient air temperature range. |  | x | x | x | x
|  |  | Water Press Drop Curve |  | Numeric | PSI |  | Water pressure drop as function of water flow rate. |  | x | x | x | x
|  |  | Water Requirement |  | Numeric | Gallons |  | Make-up water requirement. |  | x | x | x | x
|  |  | Effectiveness |  | Numeric | None |  | Ratio of the change in dry bulb temperature of the (primary) air stream to the difference between the entering dry bulb temperature of the (primary) air and the wet-bulb temperature of the (secondary) air. |  | x | x | x | x
|  |  | Latent Heat Transfer Rate |  | Numeric | BTU/Hr |  | Latent heat transfer rate to primary air flow. |  | x | x | x | x
|  |  | Sensible Heat Transfer Rate |  | Numeric | BTU/Hr |  | Sensible heat transfer rate to primary air flow. |  | x | x | x | x
|  |  | Total Heat Transfer Rate |  | Numeric | BTU/Hr |  | Total heat transfer rate to primary air flow. |  | x | x | x | x
|  |  | Water Sump Temperature |  | Numeric | Degree F |  | Water sump temperature. |  | x | x | x | x
|  | Evaporator | [5 empty] | An evaporator is a device in which a liquid refrigerant is vaporized and absorbs heat from the surrounding fluid.
|  |  | Evaporator Coolant |  | Text |  |  | The fluid used for the coolant in the evaporator. |  | x | x | x | x
|  |  | Evaporator Medium Type |  | Text |  |  | Cold Liquid: Evaporator is using liquid type of fluid to exchange heat with refrigerant. Cold Air: Evaporator is using air to exchange heat with refrigerant. |  | x | x | x | x
|  |  | External Surface Area |  | Numeric | Square Feet |  | External surface area (both primary and secondary area). |  | x | x | x | x
|  |  | Internal Refrigerant Volume |  | Numeric | Ft3/Lb |  | Internal volume of evaporator (refrigerant side). |  | x | x | x | x
|  |  | Internal Surface Area |  | Numeric | Square Feet |  | Internal surface area. |  | x | x | x | x
|  |  | Internal Water Volume |  | Numeric | Gallons |  | Internal volume of evaporator (water side). |  | x | x | x | x
|  |  | Nominal Heat Transfer Area |  | Numeric | Square Feet |  | Nominal heat transfer surface area associated with nominal overall heat transfer coefficient. |  | x | x | x | x
|  |  | Nominal Heat Transfer Coefficient |  | Numeric | BTU/(H·Ft2.oF) |  | Nominal overall heat transfer coefficient associated with nominal heat transfer area. |  | x | x | x | x
|  |  | Refrigerant Class |  | Text |  |  | Refrigerant class used by the compressor. CFC: Chlorofluorocarbons. HCFC: Hydro chlorofluorocarbons. HFC: Hydrofluorocarbons. |  | x | x | x | x
|  |  | Refrigerant Type |  | Text |  |  | Refrigerant material. |  | x | x | x | x
|  |  | Compressor Evaporator Heat Gain |  | Numeric | BTU |  | Heat gain between the evaporator outlet and the compressor inlet.
|  |  | Compressor Evaporator Pressure Drop |  | Numeric | PSI |  | Pressure drop between the evaporator outlet and the compressor inlet.
|  |  | Evaporating Temperature |  | Numeric | Degree F |  | Refrigerant evaporating temperature.
|  |  | Evaporator Mean Void Fraction |  | Numeric | None |  | Mean void fraction in evaporator.
|  |  | Exterior Heat Transfer Coefficient |  | Numeric | None |  | Exterior heat transfer coefficient associated with exterior surface area.
|  |  | Heat Rejection Rate |  | Numeric | BTU/Hr |  | Sum of the refrigeration effect and the heat equivalent of the power input to the compressor.
|  |  | Interior Heat Transfer Coefficient |  | Numeric | None |  | Interior heat transfer coefficient associated with interior surface area.
|  |  | Logarithmic Mean Temperature Difference |  | Numeric | Degree F |  | Logarithmic mean temperature difference between refrigerant and water or air.
|  |  | Refrigerant Fouling Resistance |  | Numeric | Hr·Ft2°F/BTU |  | Fouling resistance on the refrigerant side.
|  |  | U A curves |  | Text |  |  | UV = f (VExterior, VInterior), UV as a function of interior and exterior fluid flow velocity at the entrance.
|  |  | Water Fouling Resistance |  | Numeric | Hr·Ft2°F/BTU | 0.00025 | Fouling resistance on water/air side.
|  | Fan | [5 empty] | A fan is a device which imparts mechanical work on a gas. A typical usage of a fan is to induce airflow in a building services air distribution system
|  |  | Capacity Control Type |  | Text |  |  | Inlet Vane: Control by adjusting inlet vane. Variable Speed Drive: Control by variable speed drive. Blade Pitch Angle: Control by adjusting blade pitch angle. Two Speed: Control by switch between high and low speed. Discharge Damper: Control by modulating discharge damper. |  | x | x | x | x
|  |  | Efficiency Curve |  | Numeric | Percent/CFM |  | Fan efficiency =f (flow rate). |  | x | x | x | x
|  |  | Motor Drive Type |  | Text |  |  | Motor drive type: DIRECT DRIVE: Direct drive. BELT DRIVE: Belt drive. COUPLING: Coupling. OTHER: Other type of motor drive. UNKNOWN: Unknown motor drive type. |  | x | x | x | x
|  |  | Nominal Air Flow Rate |  | Numeric | Cubic Feet/Minute |  | Nominal air flow rate. |  | x | x | x | x
|  |  | Nominal Power Rate |  | Numeric | Horsepower |  | Nominal fan power rate. |  | x | x | x | x
|  |  | Nominal Rotation Speed |  | Numeric | RPM |  | Nominal fan wheel speed. |  | x | x | x | x
|  |  | Nominal Static Pressure |  | Numeric | Inches of Water |  | The static pressure within the air stream |  | x | x | x | x
|  |  | Nominal Total Pressure |  | Numeric | Inches of Water |  | Nominal total pressure rise across the fan. |  | x | x | x | x
|  |  | Operational Criteria |  | Numeric | Hours |  | Time of operation at maximum operational ambient air temperature. |  | x | x | x | x
|  |  | Operation Temperature Range |  | Numeric | Degree F |  | Allowable operation ambient air temperature range. |  | x | x | x | x
|  |  | Pressure Curve |  | Numeric | Inches/CFM |  | Pressure rise = f (flow rate). |  | x | x | x | x
|  |  | Application Of Fan |  | Text |  | Supply Air:, Return Air, Exhaust Air, Other: User Defined | The functional application of the fan.
|  |  | Coil Position |  | Text |  |  | Defines the relationship between a fan and a coil. Draw Through: Fan located downstream of the coil. Blow Through: Fan located upstream of the coil.
|  |  | Discharge Type |  | Text |  |  | Defines the type of connection at the fan discharge. Duct: Discharge into ductwork. Screen: Discharge into screen outlet. Louver: Discharge into a louver. Damper: Discharge into a damper.
|  |  | Fan Mounting Type |  | Text |  |  | Defines the method of mounting the fan in the building.
|  |  | Fraction Of Motor Heat To Air Stream |  | Numeric | BTU/Hr |  | Fraction of the motor heat released into the fluid flow.
|  |  | Impeller Diameter |  | Numeric | Inches |  | Diameter of fan wheel - used to scale performance of geometrically similar fans.
|  |  | Motor Position |  | Text |  |  | Defines the location of the motor relative to the air stream. In Airstream: Fan motor is in the air stream. Out Of Air Stream: Fan motor is out of the air stream.
|  |  | Discharge Pressure Loss |  | Numeric | Inches of Water |  | Fan discharge pressure loss associated with the discharge arrangement.
|  |  | Discharge Velocity |  | Numeric | Feet/Minute |  | The speed at which air discharges from the fan through the fan housing discharge opening.
|  |  | Drive Power Loss |  | Numeric | Horsepower |  | Fan drive power losses associated with the type of connection between the motor and the fan wheel.
|  |  | Fan Efficiency |  | Numeric | Percent |  | Fan mechanical efficiency.
|  |  | Fan Power Rate |  | Numeric | Horsepower |  | Fan power consumption.
|  |  | Fan Rotation Speed |  | Numeric | RPM |  | Fan rotation speed.
|  |  | Overall Efficiency |  | Numeric | Percent |  | Total efficiency of motor and fan.
|  |  | Shaft Power Rate |  | Numeric | Horsepower |  | Fan shaft power.
|  |  | Wheel Tip Speed |  | Numeric | Feet/Minute |  | Fan blade tip speed, typically defined as the linear speed of the tip of the fan blade furthest from the shaft.
|  |  | Centrifugal Fan |  |  |  |  | Centrifugal fan occurrence attributes attached to an instance of a fan.
|  |  |  | Arrangement | Text |  |  | Defines the fan and motor drive arrangement as defined by AMCA. |  |  | x | x | x
|  |  |  | Direction Of Rotation | Text |  | Clockwise, Counter Clockwis | The direction of the centrifugal fan wheel rotation when viewed from the drive side of the fan. . |  |  | x | x | x
|  |  |  | Discharge Position | Text |  | Top Horizontal, Top Angular Down, Down Blast, Bottom Angular Down, Bottom Angular Down, Bottom Horizontal, Bottom Angular Up, Up Blast, Top Angular Up, User Defined | Centrifugal fan discharge position. |  |  | x | x | x
|  | Filter | [5 empty] | A filter is an apparatus used to remove particulate or gaseous matter from fluids and gases.
|  |  | Final Resistance |  | Numeric | Inches of Water |  | Filter fluid resistance when replacement is required |  | x | x | x | x
|  |  | Flow Rate Range |  | Numeric | Cubic Feet/Minute |  | Possible range of fluid flowrate that can be delivered. |  | x | x | x | x
|  |  | Initial Resistance |  | Numeric | Inches of Water |  | Initial new filter fluid resistance (i.e., pressure drop at the maximum air flowrate across the filter when the filter is new per ASHRAE Standard 52.1). |  | x | x | x | x
|  |  | Nominal Filter Face Velocity |  | Numeric | Feet/Minute |  | Filter face velocity. |  | x | x | x | x
|  |  | Nominal Flowrate |  | Numeric | Cubic Feet/Minute |  | Nominal fluid flow rate through the filter. |  | x | x | x | x
|  |  | Nominal Media Surface Velocity |  | Numeric | Feet/Minute |  | Average fluid velocity at the media surface. |  | x | x | x | x
|  |  | Nominal Particle Geometric Mean Diameter |  | Numeric | Microns |  | Particle geometric mean diameter associated with nominal efficiency. |  | x | x | x | x
|  |  | Nominal Particle Geometric Standard Deviation |  | Numeric | Microns |  | Particle geometric standard deviation associated with nominal efficiency. |  | x | x | x | x
|  |  | Nominal Pressure Drop |  | Numeric | Inches of Water |  | Total pressure drop across the filter. |  | x | x | x | x
|  |  | Operation Temperature Range |  | Numeric | Degree F |  | Allowable operation ambient fluid temperature range. |  | x | x | x | x
|  |  | Weight |  | Numeric | Lbs |  | Weight of filter. |  | x | x | x | x
|  |  | Counted Efficiency |  | Numeric | Percent |  | Filter efficiency |  | x | x | x | x
|  |  | Particle Mass Holding |  | Numeric | Grams |  | Mass of particle holding in the filter. |  | x | x | x | x
|  |  | Weighted Efficiency |  | Numeric | Percent |  | Filter efficiency |  | x | x | x | x
|  |  | Air Filter |  |  |  |  | Air particle filter type attributes.
|  |  |  | Air Particle Filter Type | Text |  | Coarse Filter, Coarse Metal Screen, Coarse Cell Foams, Coarse Spun Glass, Medium Filter, HEPA Filter, ULPA Filter, etc. | A panel dry type extended surface filter is a dry-type air filter |  |  | x | x | x
|  |  |  | Counted Efficiency Curve | Numeric | Percent/Gram |  | Counted efficiency curve as a function of dust holding weight |  | x | x | x | x
|  |  |  | Dust Holding Capacity | Numeric | Grams |  | Maximum filter dust holding capacity. |  | x | x | x | x
|  |  |  | Face Surface Area | Numeric | Square Inches |  | Face area of filter frame. |  |  | x | x | x
|  |  |  | Frame Material | Text |  |  | Filter frame material. |  |  | x | x | x
|  |  |  | Media Extended Area | Numeric | Square Inches |  | Total extended media area. |  |  | x | x | x
|  |  |  | Nominal Counted Efficiency | Numeric | Percent |  | Nominal filter efficiency based the particle count concentration before and after the filter against particles with a certain size distribution. |  | x | x | x | x
|  |  |  | Nominal Weighted Efficiency | Numeric | Percent |  | Nominal filter efficiency based the particle weight concentration before and after the filter against particles with a certain size distribution. |  | x | x | x | x
|  |  |  | Pressure Drop Curve | Numeric | PSI |  | Under certain dust holding weight, DelPressure = f (fluid flowrate) |  | x | x | x | x
|  |  |  | Separation Type | Text |  |  | Air particulate filter media separation type. |  |  | x | x | x
|  |  |  | Weighted Efficiency Curve | Numeric | Percent |  | Weighted efficiency curve as a function of dust holding weight, efficiency = f (dust holding weight). |  |  | x | x | x
|  |  | Compressed Air Filter |  |  |  |  | Compressed air filter type attributes.
|  |  |  | Automatic Condensate Discharge | Text |  |  | Whether or not the condensing water or oil is discharged automatically from the filter. |  | x | x | x | x
|  |  |  | Clogging Indicator | Logic |  | True or False | Whether the filter has an indicator to display the degree of clogging of the filter. |  | x | x | x | x
|  |  |  | Compressed Air Filter Type | Text |  |  | ACTIVATED CARBON: absorbs oil vapor and odor; PARTICLE FILTER: used to absorb solid particles of medium size; COALESCENSE FILTER: used to absorb fine solid, oil, and water particles, also called micro filter |  | x | x | x | x
|  |  |  | Operation Pressure Max | Numeric | PSI |  | Maximum pressure under normal operating conditions. |  | x | x | x | x
|  |  |  | Particle Absorption Curve | Numeric | Percent |  | Ratio of particles that are removed by the filter |  | x | x | x | x
|  |  | Water Filter |  |  |  |  | Water filter type attributes.
|  |  |  | Water Filter Type | Text |  | Filtration; purficiation; softening | Further qualifies the type of water filter |  | x | x | x | x
|  | Flow Meter | [5 empty] | A flow meter is a device that is used to measure the flow rate in a system.
|  |  | Purpose |  | Text |  |  | Enumeration defining the purpose of the flow meter occurrence. |  | x | x | x | x
|  |  | Read Out Type |  | Text |  | Mechanical, Combination Pulser-Mechanical, Magnetic Sensor | Indication of the form that readout from the meter takes. |  | x | x | x | x
|  |  | Remote Reading |  | Logic |  | True or False | Indicates whether the meter has a connection for remote reading through connection of a communication device (set TRUE) or not (set FALSE). |  | x | x | x | x
|  |  | Energy Meter |  |  |  |  | Device that measures, indicates and sometimes records, the energy usage in a system.
|  |  |  | Maximum Current | Numeric | Amps |  | The maximum allowed current that a device is certified to handle. |  | x | x | x | x
|  |  |  | Multiple Tariff | Text |  |  | Indicates whether meter has built-in support for multiple tariffs (variable energy cost rates). |  | x | x | x | x
|  |  |  | Nominal Current | Numeric | Amps |  | The nominal current that is designed to be measured. |  | x | x | x | x
|  |  | Gas Meter |  |  |  |  | Device that measures, indicates and sometimes records, the volume of gas that passes through it without interrupting the flow.
|  |  |  | Connection Size | Numeric | Inches |  | Defines the size of inlet and outlet pipe connections to the meter. |  | x | x | x | x
|  |  |  | Gas Type | Text |  |  | Defines the types of gas that may be specified. |  | x | x | x | x
|  |  |  | Maximum Flow Rate | Numeric | Cubic Feet/Minute |  | Maximum rate of flow which the meter is expected to pass. |  | x | x | x | x
|  |  |  | Maximum Pressure Loss | Numeric | PSI |  | Pressure loss expected across the meter under conditions of maximum flow. |  | x | x | x | x
|  |  | Oil Meter |  |  |  |  | Device that measures, indicates and sometimes records, the volume of oil that passes through it without interrupting the flow.
|  |  |  | Connection Size | Numeric | Inches |  | Defines the size of inlet and outlet pipe connections to the meter. |  | x | x | x | x
|  |  |  | Maximum Flow Rate | Numeric | Gallons/Minute |  | Maximum rate of flow which the meter is expected to pass. |  | x | x | x | x
|  |  | Water Meter |  |  |  |  | Device that measures, indicates and sometimes records, the volume of water that passes through it without interrupting the flow.
|  |  |  | Backflow Preventer Type | Text |  |  | Identifies the type of backflow preventer installed |  | x | x | x | x
|  |  |  | Connection Size | Numeric | Inches |  | Defines the size of inlet and outlet pipe connections to the meter. |  | x | x | x | x
|  |  |  | Maximum Flow Rate | Numeric | Gallons/Minute |  | Maximum rate of flow which the meter is expected to pass. |  | x | x | x | x
|  |  |  | Maximum Pressure Loss | Numeric | PSI |  | Pressure loss expected across the meter under conditions of maximum flow. |  | x | x | x | x
|  |  |  | Type | Text |  |  | Defines the allowed values for selection of the flow meter operation type. |  | x | x | x | x
|  | Heat Exchanger | [5 empty] | A heat exchanger is a device used to provide heat transfer between non-mixing media such as plate and shell and tube heat exchangers.
|  |  | Arrangement |  | Text |  | Counter flow, Crossflow, Parallel flow, Multipass, User Defined | Defines the basic flow arrangements for the heat exchanger: |  | x | x |  | x
|  |  | Plate Exchanger |  |  |  |  | Plate heat exchanger type
|  |  |  | Number Of Plates | Numeric | None | 1,2,3… | Number of plates used by the plate heat exchanger. |  | x | x | x | x
|  | Humidifier | [5 empty] | A humidifier is a device that adds moisture into the air.
|  |  | Air Pressure Drop Curve |  | Numeric | PSI/CFM |  | Air pressure drop versus air-flow rate. |  | x | x | x | x
|  |  | Application |  | Text |  | Fixed; Portable | Humidifier application. Fixed: Humidifier installed in a ducted flow distribution system. Portable: Humidifier is not installed in a ducted flow distribution system. |  | x | x | x | x
|  |  | Internal Control |  | Text |  |  | Internal modulation control. |  | x | x | x | x
|  |  | Nominal Air Flow Rate |  | Numeric | Cubic Feet/Minute |  | Nominal rate of air flow into which water vapor is added. |  | x | x | x | x
|  |  | Nominal Moisture Gain |  | Numeric | Gallons/Day |  | Nominal rate of water vapor added into the airstream. |  | x | x | x | x
|  |  | Saturation Efficiency Curve |  | Numeric | Percent |  | Saturation efficiency as a function of the air flow rate. |  | x | x | x | x
|  |  | Water Requirement |  | Numeric | Gallons/Minute |  | Make-up water requirement. |  | x | x | x | x
|  |  | Weight |  | Numeric | Lbs |  | The weight of the humidifier. |  | x | x | x | x
|  |  | Atmospheric Pressure |  | Numeric | PSI |  | Ambient atmospheric pressure. |  | x | x | x | x
|  |  | Saturation Efficiency |  | Numeric | Percent |  | Saturation efficiency |  | x | x | x | x
|  | Pump | [5 empty] | A pump is a device which imparts mechanical work on fluids or slurries to move them through a channel or pipeline.
|  |  | Base Type |  | Text |  | Frame. Base. None User Defined | Defines general types of pump bases. |  | x | x | x | x
|  |  | Connection Size |  | Numeric | Inches |  | The connection size of the to and from the pump. |  | x | x | x | x
|  |  | Drive Connection Type |  | Text |  | Direct drive. Belt drive. Coupling. User Defined | The way the pump drive mechanism is connected to the pump. |  | x | x | x | x
|  |  | Flow Rate Range |  | Numeric | Gallons/Minute |  | Allowable range of volume of fluid being pumped against the resistance specified. |  | x | x | x | x
|  |  | Flow Resistance Range |  | Numeric | PSI |  | Allowable range of frictional resistance against which the fluid is being pumped. |  | x | x | x | x
|  |  | Flowrate |  | Numeric | Gallons/Minute |  | The actual operational fluid flowrate. |  | x | x | x | x
|  |  | Impeller Diameter |  | Numeric | Inches |  | Diameter of pump impeller - used to scale performance of geometrically similar pumps. |  | x | x | x | x
|  |  | Mechanical Efficiency |  | Numeric | Percent |  | The pumps operational mechanical efficiency. |  | x | x | x | x
|  |  | Net Positive Suction Head |  | Numeric | Feet |  | Minimum liquid pressure at the pump inlet to prevent cavitation. |  | x | x | x | x
|  |  | Nominal Rotation Speed |  | Numeric | RPM |  | Pump rotational speed under nominal conditions. |  | x | x | x | x
|  |  | Overall Efficiency |  | Numeric | Percent |  | The pump and motor overall operational efficiency. |  | x | x | x | x
|  |  | Power |  | Numeric | Horsepower |  | The actual power consumption of the pump. |  | x | x | x | x
|  |  | Pressure Rise |  | Numeric | PSI |  | The developed pressure. |  | x | x | x | x
|  |  | Rotation Speed |  | Numeric | RPM |  | Pump rotational speed. |  | x | x | x | x
|  |  | Temperature Range |  | Numeric | Degree F |  | Allowable operational range of the fluid temperature. |  | x | x | x | x
|  | Space Heater | [5 empty] | Space heaters utilize a combination of radiation and/or natural convection using a heating source such as electricity, steam or hot water to heat a limited space or area.
|  |  | Air Resistance Curve |  | Numeric | Inches of Water/CFM |  | Air resistance curve (w/ fan only); Pressure = f ( flow rate). |  | x | x | x | x
|  |  | Auxiliary Energy Source Consumption |  | Numeric | Watts |  | Auxiliary energy source consumption. |  | x | x | x | x
|  |  | Effectiveness |  | Numeric | None |  | Ratio of the real heat transfer rate to the maximum possible heat transfer rate. |  | x | x | x | x
|  |  | Energy Source |  | Text |  | Electric, Natural Gas, Propane, Hot Water, Steam, etc. | Enumeration defining the energy source or fuel combusted to generate heat if applicable |  | x | x | x | x
|  |  | Exponent |  | Numeric | None |  | Characteristic exponent, slope of log(heat output) vs log (surface temperature minus environmental temperature). |  | x | x | x | x
|  |  | Fraction Convective Heat Transfer |  | Numeric | None |  | Fraction of the total heat transfer rate as the convective heat transfer. |  | x | x | x | x
|  |  | Fraction Radiant Heat Transfer |  | Numeric | None |  | Fraction of the total heat transfer rate as the radiant heat transfer. |  | x | x | x | x
|  |  | Heat Output Rate |  | Numeric | BTU/Hr |  | Overall heat transfer rate. |  | x | x | x | x
|  |  | Heat Transfer Dimension |  | Text |  |  | Indicates how heat is transmitted according to the shape of the space heater. |  | x | x | x | x
|  |  | Heat Transfer Medium |  | Text |  |  | Enumeration defining the heat transfer medium if applicable. |  | x | x | x | x
|  |  | Number Of Panels |  | Numeric | None | 1,2,3… | Number of panels. |  | x | x | x | x
|  |  | Number Of Sections |  | Numeric | None | 1,2,3… | Number of vertical sections, measured in the direction of flow. |  | x | x | x | x
|  |  | Output Capacity |  | Numeric | Watts |  | Total nominal heat output as listed by the manufacturer. |  | x | x | x | x
|  |  | Output Capacity Curve |  | Numeric | Watts/Degree F |  | Partial output capacity curve (as a function of water temperature); Q = f (Twater). |  | x | x | x | x
|  |  | Placement Type |  | Text |  |  | Indicates how the space heater is designed to be placed. |  | x | x | x | x
|  |  | Size |  | Numeric | Inches |  | Overall body mass of the heater. |  | x | x | x | x
|  |  | Space Air Temperature |  | Numeric | Degree F |  | Dry bulb temperature in the space. |  | x | x | x | x
|  |  | Space Mean Radiant Temperature |  | Numeric | Degree F |  | Mean radiant temperature in the space. |  | x | x | x | x
|  |  | Surface Temperature |  | Numeric | Degree F |  | Average surface temperature of the component. |  | x | x | x | x
|  |  | Temperature Classification |  | Text |  |  | Enumeration defining the temperature classification of the space heater surface temperature. low temperature - surface temperature is relatively low, usually heated by hot water or electricity. high temperature - surface temperature is relatively high, usually heated by gas or steam. |  | x | x | x | x
|  |  | Thermal Efficiency |  | Numeric | Percent |  | Overall Thermal Efficiency is defined as gross energy output of the heat transfer device divided by the energy input. |  | x | x | x | x
|  |  | Thermal Mass Heat Capacity |  | Numeric |  |  | Product of component mass and specific heat. |  | x | x | x | x
|  |  | UV Curve |  | Numeric | None |  | UV = f (VExterior, VInterior), UV as a function of interior and exterior fluid flow velocity at the entrance. |  | x | x | x | x
|  |  | Convector Characteristic |  |  |  |  | Space heater type convector attributes.
|  |  |  | Convector Type | Text |  | Forced Air; Natural | Indicates the type of convector |  | x | x | x | x
|  |  | Radiator Characteristic |  |  |  |  | Space heater type radiator attributes.
|  |  |  | Radiator Type | Text |  |  | Indicates the type of radiator. |  | x | x | x | x
|  |  |  | Tubing Length | Numeric | Inches |  | Water tube length inside the component. |  | x | x | x | x
|  |  |  | Water Content | Numeric | Lbs |  | Weight of water content within the heater. |  | x | x | x | x
|  |  |  | Cooling Air Flow Rate | Numeric | Cubic Feet/Minute |  | Cooling air flow rate in the space. |  | x | x | x | x
|  |  |  | Exhaust Air Flow Rate | Numeric | Cubic Feet/Minute |  | Exhaust air flow rate in the space. |  | x | x | x | x
|  |  |  | Heating Air Flow Rate | Numeric | Cubic Feet/Minute |  | Heating air flow rate in the space. |  | x | x | x | x
|  |  |  | Space Relative Humidity | Numeric | Percent |  | The relative humidity of the space. |  | x | x | x | x
|  |  |  | Space Temperature | Numeric | Degree F |  | Temperature of the space. |  | x | x | x | x
|  |  |  | Ventilation Air Flow Rate | Numeric | Cubic Feet/Minute |  | Ventilation air flow rate in the space. |  | x | x | x | x
|  | Tank | [5 empty] | A tank is a vessel or container in which a fluid or gas is stored for later use
|  |  | Access Type |  | Text |  | Manhole, User Defined | Defines the types of access (or cover) to a tank that may be specified. Note that covers are generally specified for rectangular tanks. For cylindrical tanks, access will normally be via a manhole. |  |  | x | x | x
|  |  | Effective Capacity |  | Numeric | Gallons |  | The total effective or actual volumetric capacity of the tank. |  | x | x | x | x
|  |  | End Shape Type |  | Text |  | Semi-Elliptical, ASME Flanged Dished, ASME High Crown, Conical Dished, Standard Flanged Dished, Flanged Only, Dished Only, User Defined | Defines the types of end shapes that can be used for preformed tanks. The convention for reading these enumerated values is that for a vertical cylinder, the first value is the base and the second is the top; for a horizontal cylinder, the order of reading should be left to right. For a spherical tank, the value UNSET should be used. |  |  | x | x | x
|  |  | First Curvature Radius |  | Numeric | Inches/Feet |  | First Curvature Radius should be defined as the base or left side radius of curvature value. |  |  | x | x | x
|  |  | Nominal Capacity |  | Numeric | Gallons |  | The total nominal or design volumetric capacity of the tank. |  | x | x | x | x
|  |  | Nominal Depth |  | Numeric | Feet |  | The nominal depth of the tank. Note: Not required for a horizontal cylindrical tank. |  | x | x | x | x
|  |  | Nominal Length Or Diameter |  | Numeric | Feet |  | The nominal length or, in the case of a vertical cylindrical tank, the nominal diameter of the tank. |  | x | x | x | x
|  |  | Nominal Width Or Diameter |  | Numeric | Feet |  | The nominal width or, in the case of a horizontal cylindrical tank, the nominal diameter of the tank. Note: Not required for a vertical cylindrical tank. |  | x | x | x | x
|  |  | Number Of Sections |  | Numeric | None | 1,2,3… | Number of sections used in the construction of the tank. Default is 1. Note: All sections assumed to be the same size. |  |  | x | x | x
|  |  | Operating Weight |  | Numeric | Lbs |  | Operating weight of the tank including all of its contents. |  | x | x | x | x
|  |  | Pattern Type |  | Text |  |  | Defines the types of pattern (or shape of a tank that may be specified. |  |  | x | x | x
|  |  | Second Curvature Radius |  | Numeric | Inches/Feet |  | Second Curvature Radius should be defined as the top or right side radius of curvature value. |  |  | x | x | x
|  |  | Storage Type |  | Text |  |  | Defines the general material category intended to be stored. |  | x | x | x | x
|  |  | Has Ladder |  | Logic |  | True or False | Indication of whether the tank is provided with a ladder (set TRUE) for access to the top. If no ladder is provided then value is set FALSE. Note: No indication is given of the type of ladder (gooseneck etc.) |  |  | x | x | x
|  |  | Has Visual Indicator |  | Logic |  | True or False | Indication of whether the tank is provided with a visual indicator (set TRUE) that shows the water level in the tank. If no visual indicator is provided then value is set FALSE. |  |  | x | x | x
|  |  | Tank Composition |  | Text |  | Complex, Element, Partial, User Defined | Defines the level of element composition where. COMPLEX: A set of elementary units aggregated together to fulfill the overall required purpose. ELEMENT: A single elementary unit that may exist of itself or as an aggregation of partial units.. PARTIAL: A partial elementary unit. |  | x | x | x | x
|  |  | Expansion Tank |  |  |  |  | Specific Baseline Attributes of an expansion type tank.
|  |  |  | Charge Pressure | Numeric | PSI |  | Nominal or design operating pressure of the tank. |  | x | x | x | x
|  |  |  | Pressure Regulator Setting | Numeric | PSI |  | Pressure that is automatically maintained in the tank. |  | x | x | x | x
|  |  |  | Relief Valve Setting | Numeric | PSI |  | Pressure at which the relief valve activates. |  | x | x | x | x
|  |  | Manufactured Tank |  |  |  |  | Fixed vessel manufactured as a single unit with one or more compartments for storing a liquid.
|  |  |  | End Shape Type | Text |  | Semi-Elliptical, ASME Flanged Dished, ASME High Crown, Conical Dished, Standard Flanged Dished, Flanged Only, Dished Only, User Defined | Defines the types of end shapes that can be used for preformed tanks. The convention for reading these enumerated values is that for a vertical cylinder, the first value is the base and the second is the top; for a horizontal cylinder, the order of reading should be left to right. For a spherical tank, the value UNSET should be used. |  | x | x | x | x
|  |  |  | First Curvature Radius | Numeric | Inches/Feet |  | First Curvature Radius should be defined as the base or left side radius of curvature value. |  |  | x | x | x
|  |  |  | Pattern Type | Text |  |  | Defines the types of pattern (or shape of a tank that may be specified. |  | x | x | x | x
|  |  |  | Second Curvature Radius | Numeric | Inches/Feet |  | Second Curvature Radius should be defined as the top or right side radius of curvature value. |  |  | x | x | x
|  |  | Pressure Vessel |  |  |  |  | Specific Baseline Attributes of a pressure vessel.
|  |  |  | Charge Pressure | Numeric | PSI |  | Nominal or design operating pressure of the tank. |  | x | x | x | x
|  |  |  | Pressure Regulator Setting | Numeric | PSI |  | Pressure that is automatically maintained in the tank. |  | x | x | x | x
|  |  |  | Relief Valve Setting | Numeric | PSI |  | Pressure at which the relief valve activates. |  | x | x | x | x
|  |  | Sectional Tank |  |  |  |  | Fixed vessel constructed from sectional parts with one or more compartments for storing a liquid. Note (1): All sectional construction tanks are considered to be rectangular by default. Note (2): Generally, it is not expected that sectional construction tanks will be used for the purposes of gas storage.
|  |  |  | Number Of Sections | Numeric | None | 1,2,3… | Number of sections used in the construction of the tank Note: All sections assumed to be the same size. |  |  | x | x | x
|  |  |  | Section Length | Numeric | Inches/Feet |  | The length of a section used in the construction of the tank. |  |  | x | x | x
|  |  |  | Section Width | Numeric | Inches/Feet |  | The width of a section used in the construction of the tank. |  |  | x | x | x
|  | Tube Heat Exchanger | [5 empty] | A device that transfer heat using shell and tube configuration
|  |  | Fouling Factor |  | Numeric | Ft2-°F-Hr/BTU |  | Fouling factor of the tubes in the tube bundle. |  | x | x | x | x
|  |  | Has Turbulator |  | Logic |  | True or False | TRUE if the tube has a turbulator, FALSE if it does not. |  | x | x | x | x
|  |  | Horizontal Spacing |  | Numeric | None | 1,2,3… | Horizontal spacing between tubes in the tube bundle. |  | x | x | x | x
|  |  | In Line Row Spacing |  | Numeric | None | 1,2,3… | In-line tube row spacing. |  | x | x | x | x
|  |  | Inside Diameter |  | Numeric | Inches |  | Actual inner diameter of the tube in the tube bundle. |  | x | x | x | x
|  |  | Length |  | Numeric | Inches |  | Length of the tubes in the tube bundle. |  | x | x | x | x
|  |  | Nominal Diameter |  | Numeric | Inches |  | Nominal diameter or width of the tubes in the tube bundle. |  | x | x | x | x
|  |  | Number Of Circuits |  | Numeric | None | 1,2,3… | Number of parallel fluid tube circuits. |  | x | x | x | x
|  |  | Number Of Rows |  | Numeric | None | 1,2,3… | Number of tube rows in the tube bundle assembly. |  | x | x | x | x
|  |  | Outside Diameter |  | Numeric | Inches |  | Actual outside diameter of the tube in the tube bundle. |  | x | x | x | x
|  |  | Staggered Row Spacing |  | Numeric | None | 1,2,3… | Staggered tube row spacing. |  | x | x | x | x
|  |  | Thermal Conductivity |  | Numeric | BTU/(Hr·Ft⋅F) |  | The thermal conductivity of the tube. |  | x | x | x | x
|  |  | Vertical Spacing |  | Numeric | Inches | 1,2,3… | Vertical spacing between tubes in the tube bundle. |  | x | x | x | x
|  |  | Volume |  | Numeric | Gallons |  | Total volume of fluid in the tubes and their headers. |  | x | x | x | x
|  |  | Finned Bundle |  |  |  |  | Finned tube bundle type attributes. Contains the attributes related to the fins attached to a tube in a finned tube bundle such as is commonly found in coils.
|  |  |  | Diameter | Numeric | Inches |  | Actual diameter of a fin for circular fins only. |  | x | x | x | x
|  |  |  | Fin Corrugated Type | Text |  |  | Description of a fin corrugated type. |  | x | x | x | x
|  |  |  | Has Coating | Logic |  | True or False | TRUE if the fin has a coating, FALSE if it does not. |  | x | x | x | x
|  |  |  | Height | Numeric | Inches |  | Length of the fin as measured perpendicular to the direction of airflow. |  | x | x | x | x
|  |  |  | Length | Numeric | Inches |  | Length of the fin as measured parallel to the direction of airflow. |  | x | x | x | x
|  |  |  | Spacing | Numeric | Inches |  | Distance between fins on a tube in the tube bundle. |  | x | x | x | x
|  |  |  | Thermal Conductivity | Numeric | BTU/(Hr·Ft⋅F) |  | The thermal conductivity of the fin. |  | x | x | x | x
|  |  |  | Thickness | Numeric | Inches |  | Thickness of the fin. |  | x | x | x | x
|  | Air Conditioning Unit | [5 empty] | A unitary packaged air-conditioning unit typically used in residential or light commercial applications.
|  |  | Air Handler Construction |  | Text |  | Manufactured item, constructed on site, | Enumeration defining how the air handler might be fabricated. |  |  | x | x | x
|  |  | Air Handler Fan Coil Arrangement |  | Text |  | Blow Through, Draw Through, unknown | Enumeration defining the arrangement of the supply air fan and the cooling coil. |  |  | x | x | x
|  |  | Condenser Entering Temperature |  | Numeric | Degree F |  | Temperature of fluid entering condenser. |  | x | x | x | x
|  |  | Condenser Flowrate |  | Numeric | Gallons/Minute |  | Flow rate of fluid through the condenser. |  | x | x | x | x
|  |  | Condenser Leaving Temperature |  | Numeric | Degree F |  | Temperature of fluid leaving condenser. |  | x | x | x | x
|  |  | Cooling Efficiency |  | Numeric | None |  | Coefficient of Performance: Ratio of cooling energy output to energy input under full load operating conditions. |  | x | x | x | x
|  |  | Dual Deck |  | Logic |  | True or False | Does the Air Handler have a dual deck? TRUE = Yes, FALSE = No. |  | x | x | x | x
|  |  | Heating Capacity |  | Numeric | BTU/Hr |  | Heating capacity. |  | x | x | x | x
|  |  | Heating Efficiency |  | Numeric | None |  | Heating efficiency under full load heating conditions. |  | x | x | x | x
|  |  | Latent Cooling Capacity |  | Numeric | Tonnage |  | Latent cooling capacity. |  | x | x | x | x
|  |  | Outside Air Flowrate |  | Numeric | Cubic Feet/Minute |  | Flow rate of outside air entering the unit. |  | x | x | x | x
|  |  | Sensible Cooling Capacity |  | Numeric | BTU/Hr |  | Sensible cooling capacity. |  | x | x | x | x
|  | Valve | [5 empty] | A valve is used in a building services piping distribution system to control or modulate the flow of the fluid.
|  |  | Body Material |  | Text |  |  | Material from which the body of the valve is constructed. |  |  | x | x | x
|  |  | Close Off Rating |  | Numeric | PSI |  | Close off rating. |  | x | x | x | x
|  |  | Flow Coefficient |  | Numeric | Kv or Cv |  | Flow coefficient (the quantity of fluid that passes through a fully open valve at unit pressure drop), typically expressed as the Kv or Cv value for the valve. |  | x | x | x | x
|  |  | Measured Flow Rate |  | Numeric | Gallons/Minute |  | The rate of flow of a fluid measured across the valve. |  | x | x | x | x
|  |  | Measured Pressure Drop |  | Numeric | PSI |  | The actual pressure drop in the fluid measured across the valve. |  | x | x | x | x
|  |  | Percentage Open |  | Numeric | Percent |  | The ratio between the amount that the valve is open to the full open position of the valve. |  | x | x | x | x
|  |  | Size |  | Numeric | Inches |  | The size of the connection to the valve (or to each connection for faucets, mixing valves, etc.). |  | x | x | x | x
|  |  | Test Pressure |  | Numeric | PSI |  | The maximum pressure to which the valve has been subjected under test. |  | x | x | x | x
|  |  | Valve Mechanism |  | Text |  | Ball, Butterfly, Gate, Globe, Plug, Gland, Needle | The mechanism by which the valve function is achieved. |  |  | x | x | x
|  |  | Valve Operation |  | Text |  | Drop weight, Float, Hydraulic, Lever, Lock shield, Motorized, Pneumatic, Solenoid, Thermostatic, Wheel , User Defined | The method of valve operation. |  |  | x | x | x
|  |  | Valve Pattern |  | Text |  | Single port, Angled_2 Port, Straight_2_Port, Straight_3 _Port, Crossover_4_Port | The configuration of the ports of a valve according to either the linear route taken by a fluid flowing through the valve or by the number of ports. |  |  | x | x | x
|  |  | Working Pressure |  | Numeric | PSI |  | The normally expected maximum working pressure of the valve. |  | x | x | x | x
|  |  | Air Vent |  |  |  |  | Valve used to release air from a pipe or fitting. Note that an air release valve is constrained to have a single port pattern
|  |  |  | Is Automatic | Logic |  | True or False | Indication of whether the valve is automatically operated (TRUE) or manually operated (FALSE). |  |  | x | x | x
|  |  | Isolation Valve |  |  |  |  | A valve that is used to isolate system components. Note that an isolating valve is constrained to have a 2 port pattern.
|  |  |  | Is Normally Open | Logic |  | True or False | If TRUE, the valve is normally open. If FALSE is normally closed. |  | x | x | x | x
|  |  |  | Isolating Purpose | Text |  |  | Defines the purpose for which the isolating valve is used |  | x | x | x | x
|  |  | Pressure Reducing Valve |  |  |  |  | Valve that reduces the pressure of a fluid immediately downstream of its position in a pipeline to a preselected value or by a predetermined ratio. Note that a pressure reducing valve is constrained to have a 2 port pattern.
|  |  |  | Downstream Pressure | Numeric | PSI |  | The operating pressure of the fluid downstream of the pressure reducing valve. |  | x | x | x | x
|  |  |  | Upstream Pressure | Numeric | PSI |  | The operating pressure of the fluid upstream of the pressure reducing valve. |  | x | x | x | x
|  |  | Pressure Relief Valve |  |  |  | Spring Loaded | A valve that automatically discharges to a safe place fluid that has built up to excessive pressure in pipes or fittings. Note that a pressure relief valve is constrained to have a single port pattern.
|  |  |  | Relief Pressure | Numeric | PSI |  | The pressure at which the spring or weight in the valve is set to discharge fluid. |  | x | x | x | x
|  | Vibration Isolator | [5 empty] | A vibration isolator is a device used to minimize the effects of vibration transmissibility in a building
|  |  | Height |  | Numeric | Inches |  | Height of the vibration isolator before the application of load. |  | x | x | x | x
|  |  | Isolator Compressibility |  | Numeric | Lbs |  | The compressibility of the vibration isolator. |  | x | x | x | x
|  |  | Isolator Static Deflection |  | Numeric | Inches |  | Static deflection of the vibration isolator. |  | x | x | x | x
|  |  | Maximum Supported Weight |  | Numeric | Lbs |  | The maximum weight that can be carried by the vibration isolator. |  | x | x | x | x
|  |  | Vibration Transmissibility |  | Numeric | Percent |  | The vibration transmissibility percentage. |  | x | x | x | x

## D- Air Distribution
D- Air Distribution
Part 1 - Attribute Description | [7 empty] | Part 2 - LOD Profile |  |  |  |  | Part 3 - Example Project-Specific Milestones
[13 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute |  |  |  | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Global Attributes
None
Item-Specific Attributes
Duct
|  |  | Atmospheric Pressure | Numeric | PSI |  | Ambient atmospheric pressure. |  |  | x | x | x
|  |  | Color | Text |  |  | The color of the duct segment. Note: This is typically used for any duct segments with a painted surface which is not otherwise specified as a covering. |  |  |  |  | x
|  |  | Condition Status | Text |  | New, Existing, Demolish, Temporary, User Defined | Status of the element, predominately used in renovation or retrofitting projects. The status can be assigned to as "New" - element designed as new addition, "Existing" - element exists and remains, "Demolish" - element existed but is to be demolished, "Temporary" - element will exists only temporary (like a temporary support structure). |  |  | x | x | x
|  |  | Fluid Flow Leakage | Numeric | CFM/100SF |  | Volumetric leakage flow rate. |  |  | x | x | x
|  |  | Has Liner | Logic |  | True/False | TRUE if the fitting has interior duct insulating lining, FALSE if it does not. |  |  | x | x | x
|  |  | Interior Roughness Coefficient | Numeric |  |  | The interior roughness of the duct fitting material. |  |  | x | x | x
|  |  | Leakage Curve | Numeric | CFM/100SF |  | Leakage per unit length curve versus working pressure. If a scalar is expressed then it represents Leakage Class which is flowrate per unit area at a specified pressure rating (e.g., ASHRAE Fundamentals 2001 34.16.). |  |  | x | x | x
|  |  | Longitudinal Seam | Text |  | Lock seam, button punch snap lock | The type of seam to be used along the longitudinal axis of the duct segment. |  |  |  |  | x
|  |  | Loss Coefficient | Numeric | None |  | Dimensionless loss coefficient used for calculating fluid resistance representing the ratio of total pressure loss to velocity pressure at a referenced cross-section. |  |  | x | x | x
|  |  | Nominal Diameter Or Width | Numeric | Inches |  | The nominal diameter or width of the duct segment. |  |  | x | x | x
|  |  | Nominal Height | Numeric | Inches |  | The nominal height of the duct segment. |  |  | x | x | x
|  |  | Pressure Range | Numeric | Inches wg |  | Allowable maximum and minimum working pressure (relative to ambient pressure). |  |  | x | x | x
|  |  | Reinforcement | Text |  | angle, hat section, zee, or channel iron | The type of reinforcement, if any, used for the duct segment. |  |  |  |  | x
|  |  | Reinforcement Spacing | Numeric | Feet |  | The spacing between reinforcing elements. |  |  |  |  | x
|  |  | Shape | Text |  | Rectangular, Square, Round | Cross sectional shape. Note that this shape is uniform throughout the length of the segment. For non uniform shapes, a transition fitting should be used instead. |  |  | x | x | x
|  |  | Temperature Range | Numeric | Degree F |  | Allowable maximum and minimum temperature. |  |  | x | x | x
|  |  | Working Pressure | Numeric | Inches Wg | SMACNA | Pressure classification as defined by the authority having jurisdiction (e.g., SMACNA, etc.). |  |  | x | x | x

## D40 - Fire Protection
D40 - Fire Protection
Part 1 - Attribute Description | [8 empty] | Part 2 - LOD Profile |  |  |  |  | Part 3 - Example Project-Specific Milestones
[14 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute |  |  |  |  | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Global Attributes
| Component ID |  |  |  | Text |  |  | Part or Equipment Tag |  | x | x | x | x
| Condition Status |  |  |  | Text |  | New, Existing, Demolish, Temporary, User Defined | Status of the element, predominately used in renovation or retrofitting projects |  | x | x | x | x
| Room Number |  |  |  | Text |  |  | Room number where component to be/is installed |  | x | x | x | x
| Room Name |  |  |  | Text |  |  | Room name where component to be/is installed |  |  | x | x | x
| Story Number |  |  |  | Text |  |  | Floor or level room is located |  | x | x | x | x
| Manufacturer Name |  |  |  | Text |  |  | The organization that manufactured and/or assembled the item. |  |  |  | x | x
| Product Name |  |  |  | Text |  |  | The manufacturers model name of the product model (or product line) |  |  |  | x | x
| Model Designation |  |  |  | Text |  |  | The manufacturers model number or designator of the product model (or product line) |  |  |  | x | x
| Component characteristics | [6 empty] | Properties of individual elements of manufactured products
|  | Acquisition Date |  |  | Text |  |  | The date that the manufactured item was purchased.
|  | Assembly Place |  |  | Text |  |  | Code defining where the assembly takes place
|  | Bar Code |  |  | Text |  |  | The identity of the bar code given to an occurrence of the product.
|  | Batch Reference |  |  | Text |  |  | The identity of the batch reference from which an occurrence of a product is taken.
|  | Production Year |  |  | Numeric | Date |  | The year of production of the manufactured item.
|  | Serial Number |  |  | Text |  |  | The serial number assigned to an occurrence of a product.
| Service Life | [6 empty] | Captures the period of time that an artifact will last.
|  | Mean Time Between Failure |  |  | Numeric | Days |  | The average time duration between instances of failure of a product.
|  | Service Life Duration |  |  | Numeric | Years |  | The length or duration of a service life.
| Service Life Factors | [6 empty] | Captures various factors that impact the expected service life of elements within the system or zone.
|  | Design Level |  |  | Text |  |  | Adjustment of the service life resulting from the effect of design level employed.
|  | Indoor Environment |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the indoor environment (where appropriate).
|  | In Use Conditions |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the conditions in which components are operating.
|  | Maintenance Level |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the level or degree of maintenance applied to components.
|  | Outdoor Environment |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the outdoor environment (where appropriate)
|  | Quality Of Components |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the quality of components used.
|  | Work Execution Level |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the quality of work executed.
| Warranty | [6 empty] | A written guarantee, issued to the purchaser of an article by its manufacturer, promising to repair or replace it if necessary within a specified period of time
|  | Exclusions |  |  | Text |  |  | Items, conditions or actions that may be excluded from the warranty or that may cause the warranty to become void.
|  | Is Extended Warranty |  |  | Logic |  | True or False | Indication of whether this is an extended warranty whose duration is greater than that normally assigned
|  | Point Of Contact |  |  | Text |  |  | The organization that should be contacted for action under the terms of the warranty.
|  | Warranty Content |  |  | Text |  |  | The content of the warranty.
|  | Warranty End Date |  |  | Text |  |  | The date on which the warranty expires.
|  | Warranty Identifier |  |  | Text |  |  | The identifier assigned to a warranty.
|  | Warranty Period |  |  | Numeric | Years |  | The time duration during which a manufacturer or supplier guarantees or warrants the performance of an artefact.
|  | Warranty Start Date |  |  | Text |  |  | The date on which the warranty commences.
Item-Specific Attributes
|  | Breeching Inlet | [5 empty] | Symmetrical pipe fitting that unites two or more inlets into a single pipe
|  |  | Breeching Inlet Type |  | Text |  |  | Defines the type of breeching inlet. |  |  | x | x | x
|  |  | Coupling Type |  | Text |  |  | Defines the type coupling on the inlet of the breeching inlet. |  |  | x | x | x
|  |  | Has Caps |  | Logic |  | True or False | Does the inlet connection have protective caps. |  | x | x | x | x
|  |  | Inlet Diameter |  | Numeric | Inches |  | The inlet diameter of the breeching inlet.
|  | Hydrant | [5 empty] | Device, fitted to a pipe, through which a temporary supply of water may be provided (BS6100 330 6107) |  |  | x | x | x
|  |  | Body Color |  | Text |  | Consult local fire regulations for statutory colors | Color of the body of the hydrant. |  | x | x | x | x
|  |  | Cap Color |  | Text |  | Consult local fire regulations for statutory colors | Color of the caps of the hydrant. |  | x | x | x | x
|  |  | Discharge Flow Rate |  | Numeric | GPM |  | The volumetric rate of fluid discharge. |  | x | x | x | x
|  |  | Fire Hydrant Type |  | Text |  | DryBarrel, WetBarrel, User defined | Defines the range of hydrant types from which the required type can be selected where. |  | x | x | x | x
|  |  | Flow Class |  | Text |  | AA, A, B, C | Alphanumeric indication of the flow class of a hydrant |  | x | x | x | x
|  |  | Hose Connection Size |  | Numeric | Inches |  | The size of connections to which a hose may be connected (other than that to be linked to a pumping unit). |  | x | x | x | x
|  |  | Number Of Hose Connections |  | Numeric | None |  | The number of hose connections on the hydrant (excluding the pumper connection). |  | x | x | x | x
|  |  | Pressure Rating |  | Numeric | PSI |  | Maximum pressure that the hydrant is manufactured to withstand. |  | x | x | x | x
|  |  | Pumper Connection Size |  | Numeric | Inches |  | The size of a connection to which a fire hose may be connected that is then linked to a pumping unit.
|  |  | Water Is Potable |  | Logic |  | True or False | Indication of whether the water flow from the hydrant is potable (set TRUE) or non potable (set FALSE). |  | x | x | x | x
|  | Hose Reel | [5 empty] | A supporting framework on which a hose may be wound (BS6100 155 8201). Note that the service provided by the hose (water/foam) is determined by the context of the system onto which the hose reel is connected. |  | x | x | x | x
|  |  | Classification Authority |  | Text |  | NFPA, FEMA | The name of the authority that applies the classification of service to the hose reel |  | x | x | x | x
|  |  | Class Of Service |  | Text |  |  | A classification of usage of the hose reel that may be applied. |  | x | x | x | x
|  |  | Hose Diameter |  | Numeric | Inches |  | Notional diameter (bore) of the hose. |  | x | x | x | x
|  |  | Hose Length |  | Numeric | Feet |  | Notional length of the hose fitted to the hose reel when fully extended. |  | x | x | x | x
|  |  | Hose Nozzle Type |  | Text |  |  | Identifies the predefined types of nozzle spray pattern |  | x | x | x | x
|  |  | Hose Reel Mounting Type |  | Text |  |  | Identifies the predefined types of hose reel mounting |  | x | x | x | x
|  |  | Hose Reel Type |  | Text |  |  | Identifies the predefined types of hose arrangement
|  |  | Inlet Connection Size |  | Numeric | Inches |  | Size of the inlet connection to the hose reel. |  |  | x | x | x
|  | Sprinkler Head | [5 empty] | Device for sprinkling water from a pipe under pressure over an area (BS6100 100 3432) |  | x | x | x | x
|  |  | Activation |  | Text |  |  | Identifies the predefined methods of sprinkler activation |  |  | x | x | x
|  |  | Activation Temperature |  | Numeric | Degrees F |  | The temperature at which the object is designed to activate. |  | x | x | x | x
|  |  | Bulb Liquid Color |  | Text |  |  | The color of the liquid in the bulb for a bulb activated sprinkler |  | x | x | x | x
|  |  | Connection Size |  | Numeric | Inches |  | Size of the inlet connection to the sprinkler. |  | x | x | x | x
|  |  | Coverage Area |  | Numeric | SF |  | The area that the sprinkler is designed to protect. |  | x | x | x | x
|  |  | Discharge Coefficient |  | Numeric | Kv or Cv |  | The coefficient of flow at the sprinkler. |  |  | x | x | x
|  |  | Discharge Flow Rate |  | Numeric | GPM |  | The volumetric rate of fluid discharge. |  | x | x | x | x
|  |  | Has Deflector |  | Logic |  | True or False | Indication of whether the sprinkler has a deflector (baffle) fitted to diffuse the discharge on activation (= TRUE) or not (= FALSE). |  | x | x | x | x
|  |  | Maximum Working Pressure |  | Numeric | PSI |  | Maximum pressure that the object is manufactured to withstand. |  |  | x | x | x
|  |  | Residual Flowing Pressure |  | Numeric | PSI |  | The residual flowing pressure in the pipeline at which the discharge flow rate is determined. |  | x | x | x | x
|  |  | Response |  | Text |  |  | Identifies the predefined methods of sprinkler response
|  |  | Sprinkler Type |  | Text |  |  | Identifies the predefined types of sprinkler from which the type required may be set.
|  | Flow Meter | [5 empty] | A flow meter is a device that is used to measure the flow rate in a syste |  | x | x | x | x
|  |  | Purpose |  | Text |  |  | Enumeration defining the purpose of the flow meter occurrence. |  | x | x | x | x
|  |  | Read Out Type |  | Text |  |  | Indication of the form that readout from the meter takes. | x | x | x | x | x
|  |  | Remote Reading |  | Logic |  | True or False | Indicates whether the meter has a connection for remote reading through connection of a communication device (set TRUE) or not (set FALSE).
|  | Energy Meter | [5 empty] | Device that measures, indicates and sometimes records, the energy usage in a system. |  |  | x | x
|  |  | Maximum Current |  | Numeric | Volts |  | The maximum allowed current that a device is certified to handle. |  | x | x | x | x
|  |  | Multiple Tarriff |  | Text |  |  | Indicates whether meter has built-in support for multiple tarriffs
|  |  | Nominal Current |  | Numeric | Volts |  | The nominal current that is designed to be measured. |  | x | x | x | x
|  | Water Meter | [5 empty] | Device that measures, indicates and sometimes records, the volume of water that passes through it without interrupting the flow. |  | x | x | x | x
|  |  | Backflow Preventer Type |  | Text |  |  | Identifies the type of backflow preventer installed |  | x | x | x | x
|  |  | Connection Size |  | Numeric | Inches |  | Defines the size of inlet and outlet pipe connections to the meter. |  | x | x | x | x
|  |  | Maximum Flow Rate |  | Numeric | GPM |  | Maximum rate of flow which the meter is expected to pass. |  | x | x | x | x
|  |  | Maximum Pressure Loss |  | Numeric | PSI |  | Pressure loss expected across the meter under conditions of maximum flow.
|  |  | Type |  | Text |  |  | Defines the allowed values for selection of the flow meter operation type.
|  |  | Reference |  | Text |  |  | Reference ID for this specified type in this project (e.g. type 'A-1').
|  | Pump | [5 empty] | A pump is a device which imparts mechanical work on fluids or slurries to move them through a channel or pipeline. A typical use of a pump is to circulate chilled water or heating hot water in a building services distribution system |  | x | x | x | x
|  |  | Base Type |  | Text |  | Frame, Base, None, Other | Defines general types of pump bases. |  | x | x | x | x
|  |  | Drive Connection Type |  | Text |  | Direct drive, Belt drive, Coupling, Other | The way the pump drive mechanism is connected to the pump
|  |  | Impeller Diameter |  | Numeric | Inches |  | Diameter of pump impeller |  | x | x | x | x
|  |  | Flowrate |  | Numeric | GPM |  | The actual operational fluid flowrate. |  | x | x | x | x
|  |  | Mechanical Efficiency |  | Numeric | Percentage |  | The pumps operational mechanical efficiency. |  | x | x | x | x
|  |  | Overall Efficiency |  | Numeric | Percentage |  | The pump and motor overall operational efficiency. |  | x | x | x | x
|  |  | Power |  | Numeric | Voltage |  | The actual power consumption of the pump. |  | x | x | x | x
|  |  | Pressure Rise |  | Numeric | PSI |  | The developed pressure.
|  |  | Rotation Speed |  | Numeric | RPM |  | Pump rotational speed. |  | x | x | x | x
|  |  | Connection Size |  | Numeric | Inches |  | The connection size of the to and from the pump. |  | x | x | x | x
|  |  | Flow Rate Range |  | Numeric | GPM |  | Allowable range of volume of fluid being pumped against the resistance specified. |  | x | x | x | x
|  |  | Flow Resistance Range |  | Numeric | Kv or Cv |  | Allowable range of frictional resistance against which the fluid is being pumped. |  | x | x | x | x
|  |  | Net Positive Suction Head |  | Numeric | NPSH |  | Minimum liquid pressure at the pump inlet to prevent cavitation. | x | x | x | x | x
|  |  | Nominal Rotation Speed |  | Numeric | RPM |  | Pump rotational speed under nominal conditions. |  | x | x | x
|  |  | Temperature Range |  | Numeric | Degrees F |  | Allowable operational range of the fluid temperature.
|  | Tank | [5 empty] | A tank is a vessel or container in which a fluid or gas is stored for later use. |  | x | x | x | x
|  |  | Has Ladder |  | Logic |  | True or False | Indication of whether the tank is provided with a ladder(TRUE) or no ladder(FALSE) |  | x | x | x | x
|  |  | Has Visual Indicator |  | Logic |  | True or False | Indication of whether the tank is provided with a visual indicator(TRUE) or no visual indicator(FALSE)
|  |  | Tank Composition |  | Text |  | Complex, Element, Partial | Defines the level of element composition |  |  | x | x | x
|  |  | Access Type |  | Text |  |  | Defines the types of access (or cover) to a tank |  | x | x | x | x
|  |  | Effective Capacity |  | Numeric | Gallons |  | The total effective or actual volumetric capacity of the tank. |  |  | x | x | x
|  |  | End Shape Type |  | Text |  |  | Defines the types of end shapes that can be used for preformed tanks |  | x | x | x | x
|  |  | First Curvature Radius |  | Numeric | Inches |  | First Curvature Radius should be defined as the base or left side radius of curvature value. |  |  | x | x | x
|  |  | Nominal Capacity |  | Numeric | Gallons |  | The total nominal or design volumetric capacity of the tank. |  |  | x | x | x
|  |  | Nominal Depth |  | Numeric | Inches |  | The nominal depth of the tank |  |  | x | x | x
|  |  | Nominal Length Or Diameter |  | Numeric | Inches |  | The nominal length or, in the case of a vertical cylindrical tank, the nominal diameter of the tank. |  |  | x | x | x
|  |  | Nominal Width Or Diameter |  | Numeric | Inches |  | The nominal width or, in the case of a horizontal cylindrical tank, the nominal diameter of the tank. Note: Not required for a vertical cylindrical tank. |  | x | x | x | x
|  |  | Number Of Sections |  | Numeric | None |  | Number of sections used in the construction of the tank |  | x | x | x | x
|  |  | Operating Weight |  | Numeric | Lbs |  | Operating weight of the tank including all of its contents. |  |  | x | x | x
|  |  | Pattern Type |  | Text |  |  | Defines the types of pattern (or shape of a tank) that may be specified. | x | x | x | x | x
|  |  | Second Curvature Radius |  | Numeric | Inches |  | Second Curvature Radius should be defined as the top or right side radius of curvature value. |  | x | x | x | x
|  |  | Storage Type |  | Text |  |  | Defines the general material category intended to be stored. |  | x | x | x | x
|  | Expansion Tank | [5 empty] | A closed container used in a closed fluid distribution system to mitigate the effects of thermal expansion or water hammer. |  | x | x | x | x
|  |  | Charge Pressure |  | Numeric | PSI |  | Nominal or design operating pressure of the tank. |  | x | x | x | x
|  |  | Pressure Regulator Setting |  | Numeric | PSI |  | Pressure that is automatically maintained in the tank.
|  |  | Relief Valve Setting |  | Numeric | PSI |  | Pressure at which the relief valve activates. |  | x | x | x | x
|  |  | Manufactured Tank |  | Text |  |  | Fixed vessel manufactured as a single unit with one or more compartments |  |  | x | x | x
|  |  | End Shape Type |  | Text |  |  | Defines the types of end shapes that can be used for preformed tanks |  | x | x | x | x
|  |  | First Curvature Radius |  | Numeric | Inches |  | First Curvature Radius should be defined as the base or left side radius of curvature value. |  |  | x | x | x
|  |  | Pattern Type |  | Text |  |  | Defines the types of pattern (or shape of a tank) that may be specified.
|  |  | Second Curvature Radius |  | Numeric | Inches |  | Second Curvature Radius should be defined as the top or right side radius of curvature value. |  | x | x | x | x
|  |  | Pressure Vessel |  | Text |  |  | Common attributes of a pressure vessel. |  | x | x | x | x
|  |  | Charge Pressure |  | Numeric | PSI |  | Nominal or design operating pressure of the tank. |  | x | x | x
|  |  | Pressure Regulator Setting |  | Numeric | PSI |  | Pressure that is automatically maintained in the tank.
|  |  | Relief Valve Setting |  | Numeric | PSI |  | Pressure at which the relief valve activates. |  |  | x | x | x
|  |  | Sectional Tank |  | Text |  |  | Fixed vessel constructed from sectional parts with one or more compartments |  |  | x | x | x
|  |  | Number Of Sections |  | Numeric | None |  | Number of sections used in the construction of the tank |  |  | x | x | x
|  |  | Section Length |  | Numeric | Inches |  | The length of a section used in the construction of the tank.
|  |  | Section Width |  | Numeric | Inches |  | The width of a section used in the construction of the tank.
|  | Valve | [5 empty] | A valve is used in a building services piping distribution system to control or modulate the flow of the fluid.
|  |  | Body Material |  | Text |  |  | Material from which the body of the valve is constructed. |  | x | x | x | x
|  |  | Close Off Rating |  | Numeric | PSI |  | Close off rating. |  | x | x | x | x
|  |  | Flow Coefficient |  | Numeric | Kv or Cv |  | Flow coefficient (the quantity of fluid that passes through a fully open valve at unit pressure drop), typically expressed as the Kv or Cv value for the valve. |  | x | x | x | x
|  |  | Measured Flow Rate |  | Numeric | GPM |  | The rate of flow of a fluid measured across the valve. |  | x | x | x | x
|  |  | Measured Pressure Drop |  | Numeric | Kv or Cv |  | The actual pressure drop in the fluid measured across the valve. |  | x | x | x | x
|  |  | Percentage Open |  | Numeric | None |  | The ratio between the amount that the valve is open to the full open position of the valve. |  | x | x | x | x
|  |  | Size |  | Numeric | Inches |  | The size of the connection to the valve (or to each connection for faucets, mixing valves, etc.). |  | x | x | x | x
|  |  | Test Pressure |  | Numeric | PSI |  | The maximum pressure to which the valve has been subjected under test. |  | x | x | x
|  |  | Valve Mechanism |  | Text |  | Ball, Butterfly, Gate, Globe, Gland, Plug, Needle | The mechanism by which the valve function |  | x | x | x | x
|  |  | Valve Operation |  | Text |  | Dropwight, Float, Hydraulic, lever, Locksheild, Motorized, Pneumatic, Solenoid, Spring, Thermostatic, Chainwheel | The method of valve operation |  | x | x | x
|  |  | Valve Pattern |  | Text |  | 2Way, 3 Way, 4 Way | The configuration of the ports of a valve |  | x | x | x | x
|  |  | Working Pressure |  | Numeric | PSI |  | The normally expected maximum working pressure of the valve. |  | x | x | x | x
|  |  | Air Vent |  |  |  |  | Valve used to release air from a pipe or fitting. Note that an air release valve is constrained to have a single port pattern
|  |  |  | Is Automatic | Logic |  | True or False | Indication of whether the valve is automatically operated (TRUE) or manually operated (FALSE).
|  |  | Faucet |  |  |  |  | A small diameter valve, with a free outlet, from which water is drawn.
|  |  |  | Faucet Function | Numeric | Degrees F |  | Defines the operating temperature of a faucet that may be specified.
|  |  |  | Faucet Operation | Text |  | CeramicDisc, LeverHandle, NonConcussiveSelfClosing, Quarter Turn, QuickAction, ScrewDown, SelfClosing, TimedSelfClosing | Defines the range of ways in which a faucet can be operated
|  |  |  | Faucet Top Description | Text |  |  | Description of the operating mechanism/top of the faucet.
|  |  |  | Faucet Type | Text |  | Bib, Globe, Diverter, DividedFlowCombination, Pillar, SingleOutletCombination, SprayMixing | Defines the range of faucet types
|  |  |  | Finish | Text |  |  | Description of the finish applied to the faucet.
|  |  | Flush Valve |  |  |  |  | Valve that flushes a predetermined quantity of water to cleanse a WC, urinal or slop hopper. Note that a flushing valve is constrained to have a 2 port pattern.
|  |  |  | Flushing Rate | Numeric | GPF |  | The predetermined quantity of water to be flushed.
|  |  |  | Has Integral Shut Off Device | Logic |  | True or False | Indication of whether the flushing valve has an integral shut off device fitted (set TRUE) or not (set FALSE).
|  |  |  | Is High Pressure | Logic |  | True or False | Indication of whether the flushing valve is suitable for use on a high pressure water main (set TRUE) or not (set FALSE).
|  |  | Gas Tap Valve |  |  |  |  | A small diameter valve, used to discharge gas from a system.
|  |  |  | Has Hose Union | Logic |  | True or False | Indicates whether the gas tap is fitted with a hose union connection (= TRUE) or not (= FALSE).
|  |  | Hose Bib |  |  |  |  | A small diameter valve, used to drain water from a tank or water filled system.
|  |  |  | Has Hose Union | Logic |  | True or False | Indicates whether the drawoff cock is fitted with a hose union connection (= TRUE) or not (= FALSE).
|  |  | Isolation Valve |  |  |  |  | Valve that is used to isolate system components. Note that an isolating valve is constrained to have a 2 port pattern.
|  |  |  | Is Normally Open | Logic |  | True or False | If TRUE, the valve is normally open. If FALSE is is normally closed.
|  |  |  | Isolating Purpose | Text |  |  | Defines the purpose for which the isolating valve
|  |  | Mixing Valve |  |  |  |  | A valve where typically the temperature of the outlet is determined by mixing hot and cold water inlet flows.
|  |  |  | Mixer Control | Text |  |  | Defines the form of control of the mixing valve.
|  |  |  | Outlet Connection Size | Numeric | Inches |  | The size of the pipework connection from the mixing valve.
|  |  | Pressure Reducing Valve |  |  |  |  | Valve that reduces the pressure of a fluid immediately downstream of its position in a pipeline to a preselected value or by a predetermined ratio. Note that a pressure reducing valve is constrained to have a 2 port pattern.
|  |  |  | Downstream Pressure | Numeric | PSI |  | The operating pressure of the fluid downstream of the pressure reducing valve.
|  |  |  | Upstream Pressure | Numeric | PSI |  | The operating pressure of the fluid upstream of the pressure reducing valve.
|  |  | Pressure Relief Valve |  |  |  |  | Spring or weight loaded valve that automatically discharges to a safe place fluid that has built up to excessive pressure in pipes or fittings. Note that a pressure relief valve is constrained to have a single port pattern.
|  |  |  | Relief Pressure | Numeric | PSI |  | The pressure at which the spring or weight in the valve is set to discharge fluid.
|  | Vibration Isolator | [5 empty] | A vibration isolator is a device used to minimize the effects of vibration transmissibility in a building
|  |  | Height |  | Numeric | Inches |  | Height of the vibration isolator before tha application of load. |  |  | x | x | x
|  |  | Isolator Compressibility |  | Numeric | Inches |  | The compressibility of the vibration isolator. |  | x | x | x | x
|  |  | Isolator Static Deflection |  | Numeric | Inches |  | Static deflection of the vibration isolator. |  | x | x | x | x
|  |  | Maximum Supported Weight |  | Numeric | Lbs |  | The maximum weight that can be carried by the vibration isolator. |  |  | x | x | x
|  |  | Vibration Transmissibility |  | Numeric | Percentage |  | The vibration transmissibility percentage. |  | x | x | x | x
Note on B12: Author: name change From Moel Label To : Product Name
Note on B13: Author: Changed Name From Model Reference To Model Designation

## D- Fluid_Gas Distribution
D- Fluid_Gas Distribution
Part 1 - Attribute Description | [8 empty] | Part 2 - LOD Profile |  |  |  |  | Part 3 - Example Project-Specific Milestones
[14 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute |  |  |  |  | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Global Attributes
None
Item-Specific Attributes
Pipe Flange
|  |  | Condition Status |  | Text |  | New, Existing, Demolish, Temporary, User Defined | Status of the element, predominately used in renovation or retrofitting projects |  |  | x | x | x
|  |  | Bolthole Pitch |  | Numeric | Inches |  | Diameter of the circle along which the boltholes are placed. |  |  |  | x | x
|  |  | Bolt Size |  | Numeric | Inches |  | Size of the bolts securing the flange. |  |  |  | x | x
|  |  | Bore Size |  | Numeric | Inches |  | The nominal bore of the pipe flange. |  |  |  | x | x
|  |  | Flange Diameter |  | Numeric | Inches |  | Overall diameter of the flange. |  |  |  | x | x
|  |  | Flange Standard |  |  |  |  | Designation of the standard describing the flange table. |  |  |  | x | x
|  |  | Flange Table |  |  |  |  | Designation of the standard table to which the flange conforms. |  |  |  | x | x
|  |  | Flange Thickness |  | Numeric | Inches |  | Thickness of the material from which the pipe bend is constructed. |  |  |  | x | x
|  |  | Number Of Bolt holes |  | Numeric |  |  | Number of boltholes in the flange. |  |  |  | x | x
Pipe Fitting
|  |  | Condition Status |  | Text |  | New, Existing, Demolish, Temporary, User Defined | Status of the element, predominately used in renovation or retrofitting projects |  |  | x | x | x
|  |  | Color |  |  |  |  | The color of the pipe segment |  |  | x | x | x
|  |  | Flowrate Leakage |  |  |  |  | Leakage flowrate versus pressure difference. |  |  | x | x | x
|  |  | Interior Roughness Coefficient |  |  |  |  | The interior roughness coefficient of the pipe segment. |  |  | x | x | x
|  |  | Loss Coefficient |  |  |  |  | Dimensionless loss coefficient used for calculating fluid resistance |  |  | x | x | x
|  |  | Temperature Range |  |  |  |  | Allowable maximum and minimum temperature. |  |  | x | x | x
|  |  | Bend Attributes |  |  |  |  | Pipe fitting type attributes for bend shapes.
|  |  |  | Bend Angle | Numeric | Degrees |  | The change of direction of flow.
|  |  |  | Bend Radius | Numeric | Inches |  | The radius of bending if circular arc or zero if sharp bend.
|  |  |  | Fitting Loss Factor |  |  |  | A factor that determines the pressure loss due to friction through the fitting.
|  |  |  | Pressure Class | Text | Lbs |  | The test or rated pressure classification of the fitting.
|  |  |  | Pressure Range |  |  |  | Allowable maximum and minimum working pressure
|  |  | Tee/Cross Attributes |  |  |  |  | Pipe fitting type attributes for junction shapes.
|  |  |  | Junction Left Angle | Numeric | Degrees |  | The change of direction of flow for the left junction.
|  |  |  | Junction Left Radius | Numeric | Inches |  | The radius of bending for the left junction.
|  |  |  | Junction Right Angle | Numeric | Degrees |  | The change of direction of flow for the right junction where 0 indicates straight segment.
|  |  |  | Junction Right Radius | Numeric | Inches |  | The radius of bending for the right junction where 0 indicates sharp bend.
|  |  |  | Junction Type | Text |  | Tee, Cross | The type of junction
Pipe
|  |  | Condition Status |  | Text |  | New, Existing, Demolish, Temporary, User Defined | Status of the element, predominately used in renovation or retrofitting projects |  |  | x | x | x
|  |  | Color |  |  |  |  | The color of the pipe segment. Note: This is typically used only for plastic pipe segments. However, it may be used for any pipe segments with a painted surface which is not otherwise specified as a covering. |  |  |  | x | x
|  |  | Fluid Flow Leakage |  |  |  |  | Volumetric leakage flow rate. |  |  | x | x | x
|  |  | Gradient |  | Numeric | None |  | The gradient of the pipe segment. |  |  |  | x | x
|  |  | Inner Diameter |  | Numeric | Inches |  | The actual inner diameter of the pipe. |  |  | x | x | x
|  |  | Interior Roughness Coefficient |  | Numeric | Kv or Cv |  | The interior roughness coefficient of the pipe segment. |  |  |  | x | x
|  |  | Invert Elevation |  | Numeric | Inches |  | The invert elevation relative to the datum established for the project. |  |  | x | x | x
|  |  | Leakage Curve |  | Numeric | Kv or Cv |  | Leakage per unit length curve versus working pressure. |  |  | x | x | x
|  |  | Nominal Diameter |  | Numeric | Inches |  | The nominal diameter of the pipe segment. |  |  | x | x | x
|  |  | Outer Diameter |  | Numeric | Inches |  | The actual outer diameter of the pipe. |  |  | x | x | x
|  |  | Pressure Range |  | Numeric | PSI |  | Allowable maximum and minimum working pressure (relative to ambient pressure). |  |  | x | x | x
|  |  | Temperature Range |  | Numeric | Degrees F |  | Allowable maximum and minimum temperature. |  |  | x | x | x
|  |  | Working Pressure |  | Numeric | PSI |  | Working pressure. |  |  | x | x | x

## D50 - Electrical
D50 - Electrical
Part 1 - Attribute Description | [8 empty] | Part 2 - LOD Profile |  |  |  |  | Part 3 - Example Project-Specific Milestones
[14 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute |  |  |  |  | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Global Attributes
| Component ID |  |  |  | Text |  |  | Part or Equipment Tag |  | x | x | x | x
| Condition Status |  |  |  | Text |  | New, Existing, Demolish, Temporary, User Defined | Status of the element, predominately used in renovation or retrofitting projects |  | x | x | x | x
| Room Number |  |  |  | Text |  |  | Room number where component to be/is installed |  | x | x | x | x
| Room Name |  |  |  | Text |  |  | Room name where component to be/is installed |  |  | x | x | x
| Story Number |  |  |  | Text |  |  | Floor or level room is located |  | x | x | x | x
| Manufacturer Name |  |  |  | Text |  |  | The organization that manufactured and/or assembled the item. |  |  |  | x | x
| Product Name |  |  |  | Text |  |  | The manufacturers model name of the product model (or product line) |  |  |  | x | x
| Model Designation |  |  |  | Text |  |  | The manufacturers model number or designator of the product model (or product line) |  |  |  | x | x
| Component characteristics | [6 empty] | Properties of individual elements of manufactured products
|  | Acquisition Date |  |  | Text |  |  | The date that the manufactured item was purchased.
|  | Assembly Place |  |  | Text |  |  | Code defining where the assembly takes place
|  | Bar Code |  |  | Text |  |  | The identity of the bar code given to an occurrence of the product.
|  | Batch Reference |  |  | Text |  |  | The identity of the batch reference from which an occurrence of a product is taken.
|  | Production Year |  |  | Numeric | Date |  | The year of production of the manufactured item.
|  | Serial Number |  |  | Text |  |  | The serial number assigned to an occurrence of a product.
|  | Current |  |  | Numeric | Amps |  | The current that a device is designed to handle.
|  | Power Factor |  |  | Numeric | None |  | The ratio between the rated electrical power and the product of the device's rated current and rated voltage
|  | Enclosure Classification |  |  | Text |  |  | IEC 60529 Classification of degrees of protection provided by enclosures (IP Code).
|  | Grounded |  |  | Logic |  | True or False | Indicates whether the electrical device has a protective earth connection
|  | Frequency |  |  | Numeric | Hertz |  | The upper and lower limits of frequency for which the operation of the device is certified.
|  | Insulation Class |  |  | Text |  |  | Insulation standard classes provides basic protection information against electric shock.
|  | Line Conductor |  |  | Text |  | By color: Red, Blue, Yellow or by number 1, 2, 3, etc. | Function of a line conductor to which a device is intended to be connected where L1, L2 and L3 represent the phase lines according to IEC 60446 notation
|  | Phase |  |  | Numeric |  | Single or Three | The number of live lines that is intended to be handled by the device.
|  | Voltage |  |  | Numeric | Volts | 110Vv 220v, 480v, etc. | The voltage that a device is designed to handle.
| Service Life | [6 empty] | Captures the period of time that an artifact will last.
|  | Mean Time Between Failure |  |  | Numeric | Days |  | The average time duration between instances of failure of a product.
|  | Service Life Duration |  |  | Numeric | Years |  | The length or duration of a service life.
|  | Service Life Factors |  |  | Text |  |  | Captures various factors that impact the expected service life of elements within the system or zone.
|  | Design Level |  |  | Text |  |  | Adjustment of the service life resulting from the effect of design level employed.
|  | Indoor Environment |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the indoor environment (where appropriate).
|  | In Use Conditions |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the conditions in which components are operating.
|  | Maintenance Level |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the level or degree of maintenance applied to components.
|  | Outdoor Environment |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the outdoor environment (where appropriate)
|  | Quality Of Components |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the quality of components used.
|  | Work Execution Level |  |  | Text |  |  | Adjustment of the service life resulting from the effect of the quality of work executed.
| Warranty | [6 empty] | A written guarantee, issued to the purchaser of an article by its manufacturer, promising to repair or replace it if necessary within a specified period of time
|  | Exclusions |  |  | Text |  |  | Items, conditions or actions that may be excluded from the warranty or that may cause the warranty to become void.
|  | Is Extended Warranty |  |  | Logic |  | True or False | Indication of whether this is an extended warranty whose duration is greater than that normally assigned
|  | Point Of Contact |  |  | Text |  |  | The organization that should be contacted for action under the terms of the warranty.
|  | Warranty Content |  |  | Text |  |  | The content of the warranty.
|  | Warranty End Date |  |  | Text |  |  | The date on which the warranty expires.
|  | Warranty Identifier |  |  | Text |  |  | The identifier assigned to a warranty.
|  | Warranty Period |  |  | Numeric | Years |  | The time duration during which a manufacturer or supplier guarantees or warrants the performance of an artefact.
|  | Warranty Start Date |  |  | Text |  |  | The date on which the warranty commences.
| Electrical Properties | [6 empty] | Common electricial properties for a device
|  | Line Conductor |  |  | Text |  | By color: Red, Blue, Yellow or by number 1, 2, 3, etc. | Function of a line conductor to which a device is intended to be connected where L1, L2 and L3 represent the phase lines according to IEC 60446 notation
|  | Grounded |  |  | Logic |  | True or False | Indicates whether the electrical device has a protective earth connection
|  | Insulation Class |  |  | Text |  |  | Insulation standard classes provides basic protection information against electric shock.
|  | Enclosure Classification |  |  | Text |  |  | IEC 60529 Classification of degrees of protection provided by enclosures (IP Code).
|  | Frequency |  |  | Numeric | Hertz |  | The upper and lower limits of frequency for which the operation of the device is certified.
|  | Phase |  |  | Numeric |  | Single or Three | The number of live lines that is intended to be handled by the device.
|  | Power Factor |  |  | Numeric | None |  | The ratio between the rated electrical power and the product of the device's rated current and rated voltage
|  | Amp | [5 empty] | The current that a device is designed to handle.
|  | Voltage | [5 empty] | The voltage that a device is designed to handle.
Item-Specific Attributes
|  | Electrical Appliance | [5 empty] | Common properties for electric appliances
|  |  | Power Status |  | Logic |  | True or False | Indicates the power state of the device where True is on and False is off.
|  | Distribution Board | [5 empty] | A distribution board is a flow controller in which instances of electrical devices are brought together at a single place for a particular purpose. |  |  |  |  | x
|  |  | Main or Sub Main |  | Logic |  | True or False | Identifies if the current instance is a main distribution point or topmost level in an electrical distribution hierarchy |  |  |  | x | x
|  |  | Requires Qualifies Operator |  | Logic |  | True or False | Identifies if the current instance requires a skilled person or instructed person to perform operations on the distribution board |  |  |  |  | x
|  | Battery | [5 empty] | A device for storing energy in chemical form so that it can be released as electrical energy.
|  |  | Connected Conductor Function |  | Text |  |  | Function of the conductors to which the load is connected. |  |  |  |  | x
|  |  | Earth Fault1 Pole Maximum State |  | Numeric | Amps |  | Maximum 1 pole earth fault current provided at the point of supply i.e. the fault between 1 phase and PE/PEN. |  |  |  |  | x
|  |  | Earth Fault1 Pole Minimum State |  | Numeric | Amps |  | Minimum 1 pole earth fault current provided at the point of supply i.e. the fault between 1 phase and PE/PEN. |  |  |  |  | x
|  |  | Earth Fault1 Pole Power Factor Maximum State |  | Numeric | Amps |  | Power factor of the maximum 1 pole earth fault current provided at the point of supply i.e. the fault between 1 phase and PE/PEN. |  |  |  |  | x
|  |  | Earth Fault1 Pole Power Factor Minimum State |  | Numeric | Amps |  | Power factor of the minimum 1 pole earth fault current provided at the point of supply i.e. the fault between 1 phase and PE/PEN. |  |  |  |  | x
|  |  | Nominal Frequency |  | Numeric | Hertz |  | The nominal frequency of the supply. |  |  |  |  | x
|  |  | Nominal Supply Voltage |  | Numeric | Volts |  | The nominal voltage of the supply. |  |  |  |  | x
|  |  | Nominal Supply Voltage Offset |  | Numeric | Volts |  | The maximum and minimum allowed voltage of the supply e.g. boundaries of 380V/440V may be applied for a nominal voltage of 400V. |  |  |  |  | x
|  |  | Short Circuit1 Pole Maximum State |  | Numeric | Amps |  | Maximum 1 pole short circuit current provided at the point of supply i.e. the fault between 1 phase and N. |  |  |  |  | x
|  |  | Short Circuit1 Pole Minimum State |  | Numeric | Amps |  | Minimum 1 pole short circuit current provided at the point of supply i.e. the fault between 1 phase and N. |  |  |  |  | x
|  |  | Short Circuit1 Pole Power Factor Maximum State |  | Numeric | PF |  | Power factor of the maximum 1 pole short circuit current provided at the point of supply i.e. the fault between 1 phase and N. |  |  |  |  | x
|  |  | Short Circuit1 Pole Power Factor Minimum State |  | Numeric | PF |  | Power factor of the minimum 1 pole short circuit current provided at the point of supply i.e. the fault between 1 phase and N. |  |  |  |  | x
|  |  | Short Circuit2 Pole Minimum State |  | Numeric | Amps |  | Minimum 2 pole short circuit current provided at the point of supply. |  |  |  |  | x
|  |  | Short Circuit2 Pole Power Factor Minimum State |  | Numeric | PF |  | Power factor of the minimum 2 pole short circuit current provided at the point of supply. |  |  |  |  | x
|  |  | Short Circuit3 Pole Maximum State |  | Numeric | Amps |  | Maximum 3 pole short circuit current provided at the point of supply. |  |  |  |  | x
|  |  | Short Circuit3 Pole Power Factor Maximum State |  | Numeric | PF |  | Power factor of the maximum 3 pole short circuit current provided at the point of supply. |  |  |  |  | x
|  | Generator | [5 empty] | Defines a particular type of machine for converting mechanical energy into electrical energy.
|  |  | Electric Generator Efficiency |  | Numeric | Ratio |  | The ratio of output capacity to intake capacity. |  |  |  |  | x
|  |  | Maximum Power Output |  | Numeric | KW |  | The maximum output power rating of the engine. |  |  |  |  | x
|  |  | Start Current Factor |  | Numeric |  |  | StartCurrentFactor is multiplied to NominalCurrent and we get the start current. |  |  |  |  | x
|  | Electric Motor | [5 empty] | Defines a particular type of machine for converting mechanical energy into electrical energy.
|  |  | Electric Motor Efficiency |  | Numeric | Ratio |  | The ratio of output capacity to intake capacity. |  |  |  |  | x
|  |  | Frame Size |  | Text |  | B, C, D | Designation of the frame size according to the named range of frame sizes |  |  |  |  | x
|  |  | Has Part Winding |  | Logic |  | True or False | Indication of whether the motor is single speed, i.e. has a single winding |  |  |  |  | x
|  |  | Is Guarded |  | Logic |  | True or False | Indication of whether the motor enclosure is guarded |  |  |  |  | x
|  |  | Locked Rotor Current |  | Numeric | Amps |  | Input current when a motor armature is energized but not rotating. |  |  |  |  | x
|  |  | Maximum Power Output |  | Numeric | KW |  | The maximum output power rating of the engine. |  |  |  |  | x
|  |  | Motor Enclosure Type |  | Text |  | ODP, TEFC, TENV | A list of the available types of motor enclosure from which that required may be selected. |  |  |  |  | x
|  |  | Start Current Factor |  | Numeric |  |  | StartCurrentFactor is multiplied to NominalCurrent and to give the start current. |  |  |  |  | x
|  |  | Starting Time |  | Numeric | Seconds |  | The time (in s) needed for the motor to reach its rated speed with its driven equipment attached, starting from standstill and at the nominal voltage applied at its terminals. |  |  |  |  | x
|  |  | Te Time |  | Numeric | Seconds |  | The maximum time (in s) at which the motor could run with locked rotor when the motor is used in an EX-environment. |  |  |  |  | x
|  | Junction Box | [5 empty] | Contains cables, outlets, and/or switches for electrical power.
|  |  | Clear Depth |  | Numeric | Inches |  | Clear unobstructed depth available for cable inclusion within the junction box. |  |  |  | x | x
|  |  | I P_ Code |  | Text |  |  | IEC 60529 (1989) Classification of degrees of protection provided by enclosures (IP Code). |  |  |  |  | x
|  |  | Is External |  | Logic |  | True or False | Indication of whether the junction box type is allowed for exposure to outdoor elements |  |  |  |  | x
|  |  | Mounting Type |  | Text |  | Surface, Flush | Method of mounting to be adopted for the type of junction box. |  |  |  | x | x
|  |  | Number Of Gangs |  | Numeric |  | 1,2,3,4 | Number of slots available for switches/outlets (most commonly 1, 2, 3, or 4). |  |  | x | x | x
|  |  | Placing Type |  | Text |  |  | Location at which the type of junction box can be located. |  |  | x | x | x
|  |  | Shape Type |  | Text |  | Square, Round | Shape of the junction box. |  |  |  | x | x
|  | Lamp | [5 empty] | A lamp is an artificial light source such as a light bulb or tube. |  |  |  |  | x
|  |  | Color Appearance |  | Numeric |  |  | In both the DIN and CIE standards, artificial light sources are classified in terms of their color appearance. |  |  |  |  | x
|  |  | Color Rendering Index |  | Numeric | CRI | 1-100 | The CRI indicates how well a light source renders eight standard colors compared to perfect reference lamp with the same color temperature. |  |  |  |  | x
|  |  | Color Temperature |  | Numeric | Kelvin | 3000-4100 | The color temperatures of the commonest artificial light sources range from less than 3000K (warm white) to 4000K (intermediate) and over 5000K (daylight). |  |  |  |  | x
|  |  | Contributed Luminous Flux |  | Numeric | Lumens |  | Luminous flux is a photometric measure of radiant flux, i.e. the volume of light emitted from a light source. |  |  |  |  | x
|  |  | Lamp Ballast Type |  | Text |  | EC-A, EC-B | The type of ballast used to stabilise gas discharge by limiting the current during operation and to deliver the necessary striking voltage for starting. |  |  |  |  | x
|  |  | Lamp Compensation Type |  | Text |  |  | Identifies the form of compensation used for power factor correction and radio suppression. |  |  |  |  | x
|  |  | Lamp Maintenance Factor |  | Numeric |  |  | Non recoverable losses of luminous flux of a lamp due to lamp depreciation; i.e. the decreasing of light output of a luminaire due to aging and dirt. |  |  |  |  | x
|  |  | Light Emitter Nominal Power |  | Numeric | Watts |  | Light emitter nominal power. |  |  |  |  | x
|  |  | Spectrum |  | Numeric | nm | 380-780nm | The spectrum of radiation describes its composition with regard to wavelength. |  |  |  |  | x
|  | Light Fixture | [5 empty] | A light fixture that is considered to have a length or surface area from which it emits light in a direction
|  |  | Light Fixture Mounting Type |  | Text |  | Surface, Recessed, Wall, Pendant | A list of the available types of mounting for light fixtures from which that required may be selected. |  |  | x | x | x
|  |  | Light Fixture Placing Type |  | Text |  |  | A list of the available types of placing specification for light fixtures from which that required may be selected. |  |  | x | x | x
|  |  | Maintenance Factor |  | Numeric |  |  | The arithmetical allowance made for depreciation of lamps and reflective equipment from their initial values due to dirt, fumes, or age. |  |  |  |  | x
|  |  | Maximum Plenum Sensible Load |  | Numeric | Watts |  | Maximum or Peak sensible thermal load contributed to return air plenum by the light fixture. |  |  |  |  | x
|  |  | Maximum Space Sensible Load |  | Numeric | Watts |  | Maximum or Peak sensible thermal load contributed to the conditioned space by the light fixture. |  |  |  |  | x
|  |  | Number Of Sources |  | Numeric |  |  | Number of sources . |  |  |  |  | x
|  |  | Sensible Load To Radiant |  | Numeric | Percentage |  | Percent of sensible thermal load to radiant heat. |  |  |  |  | x
|  |  | Total Wattage |  | Numeric | Watts |  | Wattage on whole lightfitting device with all sources intact. |  |  |  |  | x
|  | Security Light | [5 empty] | A light fixture having specific purpose of directing occupants in an emergency, such as an illuminated exit sign or emergency flood light.
|  |  | Addressablility |  | Text |  |  | The type of addressability. |  |  |  |  | x
|  |  | Backup Supply System |  | Text |  |  | The type of backup supply system. |  |  |  |  | x
|  |  | Fixture Height |  | Numeirc | Inches |  | The height of the fixture, such as the text height of an exit sign. |  |  | x | x | x
|  |  | Pictogram Escape Direction |  | Text |  |  | The direction of escape pictogram. |  |  |  |  | x
|  |  | Security Lighting Type |  | Text |  |  | The type of security lighting. |  |  |  |  | x
|  |  | Self Test Function |  | Text |  |  | The type of self test function. |  |  |  |  | x
|  | Outlet | [5 empty] | An outlet is a device installed at a point to receive one or more inserted plugs for electrical power or communications.
|  |  | Is Pluggable Outlet |  | Logic |  | True or False | Indication of whether the outlet accepts a loose plug connection |  |  | x | x | x
|  |  | Number Of Sockets |  | Numeric |  |  | The number of sockets that may be connected. In case of inconsistency, sockets defined on ports take precedence. |  |  | x | x | x
|  |  | Reference |  | Text |  |  | Reference ID for this specified type in this project (e.g. type 'A-1')
|  | Breaker | [5 empty] | A protective device tripping unit breaks an electrical circuit at a separate breaking unit when a stated electric current that passes through the unit is exceeded
|  |  | Atex Verified |  | Logic |  | True or False | An indication whether the tripping_unit is verified to be applied in EX-environment or not. |  |  |  |  | x
|  |  | Limiting Terminal Size |  | Text | Circular Mils (KCM) |  | The maximum terminal size capacity of the device. |  |  |  |  | x
|  |  | Old Device |  | Logic |  | True or False | Indication whether the protection_ unit is out-dated or not. If not out-dated, the device is still for sale. |  |  |  |  | x
|  |  | Standard |  | Text |  |  | The designation of the standard applicable for the definition of the characteristics of the tripping_unit. |  |  |  |  | x
|  |  | Use In Discrimination |  | Logic |  | True or False | An indication whether the time/current tripping information can be applied in a discrimination analysis or not. |  |  |  |  | x
|  |  | Curve |  |  |  |  | A coherent set of attributes representing a curve for let-through energy of a protective device.
|  |  |  | Breaker Unit Curve | Numeric, 2-16 digits, Cartesian Coord Set | Amps |  | A curve that establishes the let through energy of a breaker unit when a particular prospective current is applied.
|  |  |  | Nominal Current | Numeric | Amps |  | A set of nominal currents in [A] for which the data of this instance is valid.
|  |  |  | Voltage Level | Numeric | Volts |  | The voltage levels of the protective device for which the data of the instance is valid.
|  |  | Fuse Curve |  |  |  |  | A coherent set of attributes representing curves for melting- and breaking-energy of a fuse.
|  |  |  | Breaker Unit Fuse Breaking Curve | Numeric, 2-8 digits, Cartesian Coord Set | Amps |  | The let through breaking energy of a breaker unit when a particular prospective breaking current is applied.
|  |  |  | Breaker Unit Fuse Melting Curve | Numeric, 2-8 digits, Cartesian Coord Set | Amps |  | A curve that establishes the energy required to melt the fuse of a breaker unit when a particular prospective melting current is applied.
|  |  |  | Voltage Level | Numeric | Volts |  | The voltage levels of the fuse for which the data of the instance is valid. More than one value may be selected in the enumeration.
|  |  | IPI Curve |  |  |  |  | A coherent set of attributes representing curves for let-through currents of a protective device.
|  |  |  | Breaker Unit I P I Curve | Numeric, 2-16 digits, Cartesian Coord Set | Amps |  | The let through peak current of a breaker unit when a particular prospective current is applied.
|  |  |  | Nominal Current | Numeric | Amps |  | A set of nominal currents in [A] for which the data of this instance is valid. At least one value shall be provided.
|  |  |  | Voltage Level | Numeric | Volts |  | The voltage level of the protective device for which the data of the instance is valid. More than one value may be selected in the enumeration.
|  |  | Breaker Capacity |  |  |  |  | A coherent set of attributes representing the breaking capacities of an MCB.
|  |  |  | I C N60898 | Numeric | Amps |  | The nominal breaking capacity in [A] for an MCB tested in accordance with the IEC 60898 series.
|  |  |  | I C S60898 | Numeric | Amps |  | The service breaking capacity in [A] for an MCB tested in accordance with the IEC 60898 series.
|  |  |  | I C S60947 | Numeric | Amps |  | The service breaking capacity in [A] for an MCB tested in accordance with the IEC 60947 series.
|  |  |  | I C U60947 | Numeric | Amps |  | The ultimate breaking capacity in [A] for an MCB tested in accordance with the IEC 60947 series.
|  |  |  | Nominal Currents | Numeric | Amps |  | A set of nominal currents in [A] for which the data of this instance is valid. At least one value shall be provided.
|  |  |  | Power Loss | Numeric | Watts |  | The power loss in [W] per pole of the MCB when the nominal current is flowing through the MCB.
|  |  |  | Voltage Level | Numeric | Volts |  | The voltage levels for which the data of the instance is valid. More than one value may be selected in the enumeration.
|  |  | Motor Protection |  |  |  |  | A coherent set of attributes representing different capacities of a a motor protection device, defined in accordance with IEC 60947.
|  |  |  | I C M60947 | Numeric | Amps |  | The making capacity in [A] for a circuit breaker or motor protection device tested in accordance with the IEC 60947 series.
|  |  |  | I C S60947 | Numeric | Amps |  | The service breaking capacity in [A] for a circuit breaker or motor protection device tested in accordance with the IEC 60947 series.
|  |  |  | I C U60947 | Numeric | Amps |  | The ultimate breaking capacity in [A] for a circuit breaker or motor protection device tested in accordance with the IEC 60947 series.
|  |  |  | I C W60947 | Numeric | Amps |  | The thermal withstand current in [A] for a circuit breaker or motor protection device tested in accordance with the IEC 60947 series. The value shall be related to 1 s.
|  |  |  | Performance Classes | Text |  | B, C, N, S, H, L, V | A set of designations of performance classes for the breaker unit for which the data of this instance is valid.
|  |  |  | Voltage Level | Numeric | Volts |  | The voltage levels for which the data of the instance is valid. More than one value may be selected in the enumeration.
|  |  | Characteristics |  |  |  |  | Properties that are applied to an occurrence of a protective device.
|  |  |  | Ground Fault Current Set Value | Numeric | Amps |  | Ground fault current set value. The set value of the ground tripping current if adjustable.
|  |  |  | Ground Fault Function | Logic |  | True or False | A flag indicating that the ground fault function of the device is used.
|  |  |  | Ground Faulti2t Function | Logic |  | True or False | A flag indicating that the I2t ground fault function of the device is used.
|  |  |  | Ground Fault Tripping Time | Numeric | Seconds |  | Ground fault tripping time. The set value of the ground fault tripping current if adjustable.
|  |  |  | Instantaneous Current Set Value | Numeric | Amps |  | Instantaneous current set value. The set value of the instantaneous tripping current if adjustable.
|  |  |  | Instantaneous Tripping Time | Numeric | Seconds |  | Instantaneous tripping time. The set value of the instantaneous tripping time if adjustable.
|  |  |  | Long Time Current Set Value | Numeric | Amps |  | Long time current set value. The set value of the long time tripping current if adjustable.
|  |  |  | Long Time Delay | Numeric | Seconds |  | Long time delay. The set value of the long time time-delay if adjustable.
|  |  |  | Long Time Function | Logic |  | True or False | A flag indicating that the long time function (i.e. the thermal tripping) of the device is used.
|  |  |  | Pole Usage | Numeric |  | 1,3 | Pole usage.
|  |  |  | Short Time Current Set Value | Numeric | Amps |  | Short time current set value. The set value of the long time tripping current if adjustable.
|  |  |  | Short Time Function | Logic |  | True or False | A flag indicating that the short time function of the device is used.
|  |  |  | Short Timei2t Function | Logic |  | True or False | A flag indicating that the I2t short time function of the device is used.
|  |  |  | Short Time Tripping Time | Numeric | Seconds |  | Short time tripping time. The set value of the short time tripping time if adjustable.
|  |  | Trip Curve |  |  |  |  | Tripping curves are applied to thermal, thermal magnetic or MCB_RCD tripping units (i.e. tripping units having type property sets for thermal, thermal magnetic or MCB_RCD tripping defined). They are not applied to electronic tripping units.
|  |  |  | Tripping Curve | Numeric, 2-16 digits, Cartesian Coord Set | Amps |  | A curve that establishes the release time of a tripping unit when a particular prospective current is applied.
|  |  |  | Tripping Curve Type | Text |  |  | The type of tripping curve that is represented by the property set.
|  |  | G Curve |  |  |  |  | Tripping functions are applied to electronic tripping units (i.e. tripping units having type property sets for electronic tripping defined). They are not applied to thermal, thermal magnetic or RCD tripping units.
|  |  |  | Current Tolerance1 | Numeric | Percentage |  | The tolerance for the current of time/current-curve in [%].
|  |  |  | Current Tolerance2 | Numeric | Percentage |  | The tolerance for the current of time/current-curve in [%] valid for times above CurrentTolereanceLimit1.
|  |  |  | Current Tolerance Limit1 | Numeric | Seconds |  | The time limit in [s] limiting the application of CurrentTolerance1, if any. If the value is set to 0, the value of the CurrentTolerance1 is valid for the whole time/current-curve.
|  |  |  | External Adjusted | Logic |  | True or False | An indication if the ground fault protection may be adjusted according to an external current coil or not.
|  |  |  | Is Current Tolerance Positive Only | Logic |  | True or False | Indication whether the value of CurrentTolerance1 is provided as a positive tolereance only or not. If not, the value is proved as a pluss/minus tolerance.
|  |  |  | Is Selectable | Logic |  | True or False | Indication whether the S-function can be switched off or not.
|  |  |  | Is Time Tolerance Positive Only | Logic |  | True or False | Indication whether the value of TimeTolerance1 is provided as a positive tolereance only or not. If not, the value is proved as a pluss/minus tolerance.
|  |  |  | Nominal Current Adjusted | Logic |  | True or False | An indication if the tripping currents of the short time protection is related to the nominal current multiplied with the actual setting of the current adjustment, if any, of the long time protection part of the protective device, or not.
|  |  |  | Release Current | Numeric | Amps |  | The release current in [x In] for the initial tripping of the S-function.
|  |  |  | Release Current I2t End | Numeric | Amps |  | The release current in [x In] for the end point of the I2t tripping curve of the G-function, if any. The value of ReleaseCurrentI2tEnd shall be larger than ReleaseCurrentI2tStart.
|  |  |  | Release Current I2t Start | Numeric | Amps |  | The release current in [x In] for the start point of the I2t tripping curve of the G-function, if any.
|  |  |  | Release Time | Numeric | Seconds |  | The release time in [s] for the initial tripping of the relevant part. This time indicates that for current lower than the indicated release current, the tripping time will be longer than the indicated release time. The value is given as a mean value.
|  |  |  | Release Time I2t End | Numeric | Seconds |  | The release time in [s] for the end point of the I2 tripping curve of the G-function, if any. The value of ReleaseTimeI2tEnd shall be lower than ReleaseTimeI2tStart.
|  |  |  | Release Time I2t Start | Numeric | Seconds |  | The release time in [s] for the start point of the I2t tripping curve of the G-function, if any.
|  |  |  | Time Tolerance1 | Numeric | Percentage |  | The tolerance for the time of time/current-curve in [%].
|  |  |  | Time Tolerance2 | Numeric | Percentage |  | The tolerance for the time of the time/current-curve in [%] valid for currents above TimeToleranceLimit1.
|  |  |  | Time Tolerance Limit1 | Numeric | Amps |  | The current limit in [x In] limiting the application of TimeTolerance1, if any. If the value is set to 0, the value of the TimeTolerance1 is valid for the whole time/current-curve.
|  |  | I Curve |  |  |  |  | Tripping functions are applied to electronic tripping units (i.e. tripping units having type property sets for electronic tripping defined). They are not applied to thermal, thermal magnetic or RCD tripping units. This property set represent the instantaneous time protection (I-curve) of an electronic protection device.
|  |  |  | Current Tolerance1 | Numeric | Percentage |  | The tolerance for the current of time/current-curve in [%].
|  |  |  | Current Tolerance2 | Numeric | Percentage |  | The tolerance for the current of time/current-curve in [%] valid for times above CurrentTolereanceLimit1.
|  |  |  | Current Tolerance Limit1 | Numeric | Seconds |  | The time limit in [s] limiting the application of CurrentTolerance1, if any. If the value is set to 0, the value of the CurrentTolerance1 is valid for the whole time/current-curve.
|  |  |  | Is Current Tolerance Positive Only | Logic |  | True or False | Indication whether the value of CurrentTolerance1 is provided as a positive tolereance only or not. If not, the value is proved as a pluss/minus tolerance.
|  |  |  | Is Off When S Function On | Logic |  | True or False | Indication whether the I-function is automatically switched off when the S-function is switched on.
|  |  |  | Is Selectable | Logic |  | True or False | Indication whether the S-function can be switched off or not.
|  |  |  | Is Time Tolerance Positive Only | Logic |  | True or False | Indication whether the value of TimeTolerance1 is provided as a positive tolereance only or not. If not, the value is proved as a pluss/minus tolerance.
|  |  |  | Max Adjustment X_ I C S | Numeric | Amps |  | Provides the maximum setting value for the available current adjustment in relation to the Ics breaking capacity of the protection device of which the actual tripping unit is a part of.
|  |  |  | Nominal Current Adjusted | Logic |  | True or False | An indication if the tripping currents of the short time protection is related to the nominal current multiplied with the actual setting of the current adjustment, if any, of the long time protection part of the protective device, or not.
|  |  |  | Release Current | Numeric | Amps |  | The release current in [x In] for the initial tripping of the S-function.
|  |  |  | Release Time | Numeric | Seconds |  | The release time in [s] for the initial tripping of the relevant part.
|  |  |  | Time Tolerance1 | Numeric | Percentage |  | The tolerance for the time of time/current-curve in [%].
|  |  |  | Time Tolerance2 | Numeric | Percentage |  | The tolerance for the time of the time/current-curve in [%] valid for currents above TimeToleranceLimit1.
|  |  |  | Time Tolerance Limit1 | Numeric | Amps |  | The current limit in [x In] limiting the application of TimeTolerance1, if any. If the value is set to 0, the value of the TimeTolerance1 is valid for the whole time/current-curve.
|  |  | L Curve |  |  |  |  | Tripping functions are applied to electronic tripping units (i.e. tripping units having type property sets for electronic tripping defined). They are not applied to thermal, thermal magnetic or RCD tripping units. This property set represent the long time protection (L-curve) of an electronic protection device
|  |  |  | Is Selectable | Logic |  | True or False | Indication whether the L-function can be switched off or not.
|  |  |  | Lower Current1 | Numeric | Amps |  | The current in [x In], indicating that for currents smaller than LowerCurrent1 the I2t part of the L-function will not trip the current,
|  |  |  | Lower Current2 | Numeric | Amps |  | The current in [x In], indicating the upper current limit of the lower time/current curve of the I2t part of the L-function.
|  |  |  | Lower Time1 | Numeric | Seconds |  | The time in [s], indicating that tripping times of the lower time/current curve lower than LowerTime1 is determined by the I2t part of the L-function.
|  |  |  | Lower Time2 | Numeric | Seconds |  | The time in [s], indicating the tripping times of the upper time/current curve at the LowerCurrent2.
|  |  |  | Upper Current1 | Numeric | Amps |  | The current in [x In], indicating that for currents larger than UpperCurrent1 the I2t part of the L-function will trip the current.
|  |  |  | Upper Current2 | Numeric | Amps |  | The current in [x In], indicating the upper current limit of the upper time/current curve of the I2t part of the L-function.
|  |  |  | Upper Time1 | Numeric | Seconds |  | The time in [s], indicating that tripping times of the upper time/current curve lower than UpperTime1 is determined by the I2t part of the L-function.
|  |  |  | Upper Time2 | Numeric | Seconds |  | The time in [s], indicating the tripping times of the upper time/current curve at the UpperCurrent2.
|  |  | S Curve |  |  |  |  | Tripping functions are applied to electronic tripping units (i.e. tripping units having type property sets for electronic tripping defined). They are not applied to thermal, thermal magnetic or RCD tripping units. This property set represent the short time protection (S-curve) of an electronic protection device.
|  |  |  | Current Tolerance1 | Numeric | Percentage |  | The tolerance for the current of time/current-curve in [%].
|  |  |  | Current Tolerance2 | Numeric | Percentage |  | The tolerance for the current of time/current-curve in [%] valid for times above CurrentTolereanceLimit1.
|  |  |  | Current Tolerance Limit1 | Numeric | Seconds |  | The time limit in [s] limiting the application of CurrentTolerance1, if any. If the value is set to 0, the value of the CurrentTolerance1 is valid for the whole time/current-curve.
|  |  |  | Is Current Tolerance Positive Only | Logic |  | True or False | Indication whether the value of CurrentTolerance1 is provided as a positive tolereance only or not. If not, the value is proved as a pluss/minus tolerance.
|  |  |  | Is Off When Lfunction On | Logic |  | True or False | Indication whether the S-function is automatically switched off when the I-function is switched on.
|  |  |  | Is Selectable | Logic |  | True or False | Indication whether the S-function can be switched off or not.
|  |  |  | Is Time Tolerance Positive Only | Logic |  | True or False | Indication whether the value of TimeTolerance1 is provided as a positive tolereance only or not. If not, the value is proved as a pluss/minus tolerance.
|  |  |  | Nominal Current Adjusted | Logic |  | True or False | An indication if the tripping currents of the short time protection is related to the nominal current multiplied with the actual setting of the current adjustment, if any, of the long time protection part of the protective device, or not.
|  |  |  | Release Current | Numeric | Amps |  | The release current in [x In] for the initial tripping of the S-function.
|  |  |  | Release Current I2t End | Numeric | Amps |  | The release current in [x In] for the end point of the I2t tripping curve of the S-function, if any. The value of ReleaseCurrentI2tEnd shall be larger than ReleaseCurrentI2tStart.
|  |  |  | Release Current I2t Start | Numeric | Amps |  | The release current in [x In] for the start point of the I2t tripping curve of the S-function, if any.
|  |  |  | Release Time | Numeric | Seconds |  | The release time in [s] for the initial tripping of the relevant part. This time indicates that for current lower than the indicated release current, the tripping time will be longer than the indicated release time. The value is given as a mean value.
|  |  |  | Release Time I2t End | Numeric | Seconds |  | The release time in [s] for the end point of the I2 tripping curve of the S-function, if any. The value of ReleaseTimeI2tEnd shall be lower than ReleaseTimeI2tStart.
|  |  |  | Release Time I2t Start | Numeric | Seconds |  | The release time in [s] for the start point of the I2t tripping curve of the S-function, if any
|  |  |  | Time Tolerance1 | Numeric | Percentage |  | The tolerance for the time of time/current-curve in [%].
|  |  |  | Time Tolerance2 | Numeric | Percentage |  | The tolerance for the time of the time/current-curve in [%] valid for currents above TimeToleranceLimit1.
|  |  |  | Time Tolerance Limit1 | Numeric | Amps |  | The current limit in [x In] limiting the application of TimeTolerance1, if any. If the value is set to 0, the value of the TimeTolerance1 is valid for the whole time/current-curve.
|  |  | Current Adjustment Values |  |  |  |  | A set of current adjustment values that may be applied to an electronic or thermal tripping unit type.
|  |  |  | Adjustment Designation | Text |  |  | The desgnation on the device for the adjustment.
|  |  |  | Adjustment Range | Numeric | Amps |  | Upper and lower current adjustment limits for an AdjustmentValueType = RANGE. Note that this property should not have a value for an AdjustmentValueType = LIST.
|  |  |  | Adjustment Range Step Value | Numeric | Amps |  | Step value of current adjustment for an AdjustmentValueType = RANGE. Note that this property should not have a value for an AdjustmentValueType = LIST.
|  |  |  | Adjustment Values | Numeric | Amps |  | A list of current adjustment values that may be applied to a tripping unit for an AdjustmentValueType = LIST.
|  |  |  | Adjustment Value Type | Text |  |  | The type of adjustment value that is applied through the property set. This determines the properties that should be asserted.
|  |  | Time Adjustment Values |  |  |  |  | A set of time adjustment values that may be applied to an electronic or thermal tripping unit type.
|  |  |  | Adjustment Designation | Text |  |  | The desgnation on the device for the adjustment.
|  |  |  | Adjustment Range | Numeric | Seconds |  | Upper and lower time adjustment limits for an AdjustmentValueType = RANGE
|  |  |  | Adjustment Range Step Value | Numeric | Seconds |  | Step value of time adjustment for an AdjustmentValueType = RANGE
|  |  |  | Adjustment Values | Numeric | Seconds |  | A list of time adjustment values that may be applied to a tripping unit for an AdjustmentValueType = LIST.
|  |  |  | Adjustment Value Type | Text |  |  | The type of adjustment value that is applied through the property set
|  |  |  | Current For Time Delay | Numeric | Amps |  | The tripping current in [x In] at which the time delay is specified
|  |  |  | I2 T Applicability | Logic |  | True or False | The applicability of the time adjustment related to the tripping function.
|  |  | Electro Magnetic Type |  |  |  |  | Information on tripping units that are electrically or magnetically tripped.
|  |  |  | Curve Designation | Text |  |  | The designation of the trippingcurve given by the manufacturer
|  |  |  | Defined Temperature | Numeric | Degrees C |  | The ambient temperature at which the thermal current/time-curve associated with this protection device is defined.
|  |  |  | Electro Magnetic Tripping Unit Type | Text |  | Overload, none special, short circuit, motor protection and bi-metal tripping | A list of the available types of electric magnetic tripping unit from which that required may be selected.
|  |  |  | I1 | Numeric | Amps |  | The (thermal) lower testing current limit in [x In], indicating that for currents lower than I1, the tripping time shall be longer than the associated tripping time, T2.
|  |  |  | I2 | Numeric | Amps |  | The (thermal) upper testing current limit in [x In], indicating that for currents larger than I2, the tripping time shall be shorter than the associated tripping time, T2.
|  |  |  | I4 | Numeric | Amps |  | The lower electromagnetic testing current limit in [x In], indicating that for currents lower than I4, the tripping time shall be longer than the associated tripping time, T5, i.e. the device shall not trip instantaneous.
|  |  |  | I5 | Numeric | Amps |  | The upper electromagnetic testing current limit in [x In], indicating that for currents larger than I5, the tripping time shall be shorter than or equal to the associated tripping time, T5, i.e. the device shall trip instantaneous.
|  |  |  | T2 | Numeric | Seconds |  | The (thermal) testing time in [s] associated with the testing currents I1 and I2.
|  |  |  | T5 | Numeric | Seconds |  | The electromagnetic testing time in [s] associated with the testing currents I4 and I5, i.e. electromagnetic tripping time
|  |  |  | Temperature Factor | Text |  |  | The correction factor (typically measured as %/deg K) for adjusting the thermal current/time to an ambient temperature different from the value given by the defined temperature.
|  |  | Electronic Type |  |  |  |  | Information on tripping units that are electronically tripped.
|  |  |  | Electronic Tripping Unit Type | Text |  |  | A list of the available types of electronic tripping unit from which that required may be selected.
|  |  |  | N_ Protection | Logic |  | True or False | An indication whether the electronic tripping unit has separate protection for the N conductor, or not.
|  |  |  | N_ Protection_100 | Logic |  | True or False | An indication whether the electronic tripping unit is tripping if the current in the N conductor is more than 100% of that of the phase conductors.
|  |  |  | N_ Protection_50 | Logic |  | True or False | An indication whether the electronic tripping unit is tripping if the current in the N conductor is more than 50% of that of the phase conductors.
|  |  |  | N_ Protection_ Select | Logic |  | True or False | An indication whether the use of the N_Protection can be selected by the user or not.
|  |  |  | Nominal Currents | Numeric |  |  | A set of values providing information on available modules (chips) for setting the nominal current of the protective device.
|  |  | Residual Current |  |  |  |  | Information on tripping units that are activated by residual current.
|  |  |  | Tripping Unit Release Current | Numeric | mA |  | The value of tripping or residual current for which the device has the possibility to be equipped. The values are given in mA.
|  |  | Thermal Type |  |  |  |  | Information on tripping units that are thermally tripped.
|  |  |  | Curve Designation | Text |  |  | The designation of the trippingcurve given by the manufacturer. For a MCB the designation should be in accordance with the designations given in IEC 60898.
|  |  |  | Defined Temperature | Numeric | Degrees C |  | The ambient temperature at which the thermal current/time-curve associated with this protection device is defined.
|  |  |  | I1 | Numeric | Amps |  | The (thermal) lower testing current limit in [x In], indicating that for currents lower than I1, the tripping time shall be longer than the associated tripping time, T2.
|  |  |  | I2 | Numeric | Amps |  | The (thermal) upper testing current limit in [x In], indicating that for currents larger than I2, the tripping time shall be shorter than the associated tripping time, T2.
|  |  |  | T2 | Numeric | Seconds |  | The (thermal) testing time in [s] associated with the testing currents I1 and I2.
|  |  |  | Temperature Factor | Text |  |  | The correction factor (typically measured as %/deg K) for adjusting the thermal current/time to an ambient temperature different from the value given by the defined temperature.
|  |  |  | Thermal Tripping Unit Type | Text |  |  | A list of the available types of thermal tripping unit from which that required may be selected.
|  |  | Circuit Breaker Type |  |  |  |  | A coherent set of attributes representing different capacities of a circuit breaker or of a motor protection device, defined in accordance with IEC 60947.
|  |  |  | I C M60947 | Numeric | Amps |  | The making capacity in [A] for a circuit breaker or motor protection device tested in accordance with the IEC 60947 series.
|  |  |  | I C S60947 | Numeric | Amps |  | The service breaking capacity in [A] for a circuit breaker or motor protection device tested in accordance with the IEC 60947 series.
|  |  |  | I C U60947 | Numeric | Amps |  | The ultimate breaking capacity in [A] for a circuit breaker or motor protection device tested in accordance with the IEC 60947 series.
|  |  |  | I C W60947 | Numeric | Amps |  | The thermal withstand current in [A] for a circuit breaker or motor protection device tested in accordance with the IEC 60947 series. The value shall be related to 1 s.
|  |  |  | Performance Classes | Text |  | B, C, N, S, H, L, V | A set of designations of performance classes for the breaker unit for which the data of this instance is valid.
|  |  |  | Voltage Level | Numeric | Volts |  | The voltage levels for which the data of the instance is valid. More than one value may be selected in the enumeration.
|  |  | Ground Fault Type |  |  |  |  | An earth failure device acts to protect people and equipment from the effects of current leakage.
|  |  |  | Earth Failure Device Type | Text |  |  | A list of the available types of circuit breaker from which that required may be selected
|  |  |  | Sensitivity | Numeric | Amps (RMS) |  | The rated rms value of the vector sum of the instantaneous currents flowing in the main circuits of the device which causes the device to operate under specified conditions.
|  |  | Fuse Disconnect Type |  |  |  |  | A coherent set of attributes representing the breakeing capacity of a fuse, defined in accordance with IEC 60269.
|  |  |  | Fuse Disconnector Type | Text |  | EngineProtectionDevice, FuseSwitchDisconnector, HRC, OverloadProtectionDevice, SemiconductorFuse, SwitchDisconnectorFuse | A list of the available types of fuse disconnector from which that required may be selected
|  |  |  | I C60269 | Numeric | Amps |  | The breaking capacity in [A] for fuses in accordance with the IEC 60269 series.
|  |  |  | Power Loss | Numeric | Watts |  | The power loss in [W] of the fuse when the nominal current is flowing through the fuse.
|  |  |  | Voltage Level | Numeric | Volts |  | The voltage levels for which the data of the instance is valid. More than one value may be selected in the enumeration.
|  |  | Current Circuit Breaker |  |  |  |  | A residual current circuit breaker opens, closes or isolates a circuit and has short circuit and overload protection.
|  |  |  | Sensitivity | Numeric | Amps |  | Current leakage to an unwanted leading path during normal operation (IEC 151-14-49).
|  |  | Current Switch |  |  |  |  | A residual current switch opens, closes or isolates a circuit and has no short circuit or overload protection.
|  |  |  | Sensitivity | Numeric | Amps |  | Current leakage to an unwanted leading path during normal operation (IEC 151-14-49).
|  |  | Variable Resistor |  |  |  |  | A high voltage surge protection device.
|  |  |  | Varistor Type | Text |  |  | A list of the available types of varistor from which that required may be selected.
|  | Switch | [5 empty] | A switch is used in a cable distribution system (electrical circuit) to control or modulate the flow of electricity
|  |  | Has Lock |  | Logic |  | True or False | Indication of whether a switching device has a key operated lock |  |  |  |  | x
|  |  | Is Illuminated |  | Logic |  | True or False | An indication of whether there is an illuminated indicator to show that the switch is on |  |  |  |  | x
|  |  | Legend |  | Text |  |  | A text inscribed or applied to the switch as a legend to indicate purpose or function. |  |  |  |  | x
|  |  | Number Of Gangs |  | Numeric |  | 1,2,3,4 | Number of gangs/buttons on this switch. |  |  |  | x | x
|  |  | Set Point |  | Logic |  | 0,1 | Indicates the setpoint and label. For toggle switches, there are two positions, 0 for off and 1 for on. |  |  |  |  | x
|  |  | Switch Function |  | Text |  |  | Indicates types of switches which differs in functionality. |  |  |  |  | x
|  |  | Contact |  |  |  |  | An electrical device used to control the flow of power in a circuit on or off.
|  |  |  | Contactor Type | Text |  | CapacitorSwitching, LowCurrent, MagneticLatching, MechanicalLatching, Modular, Reversing, Standard | A list of the available types of contactor from which that required may be selected
|  |  | Dimmer |  |  |  |  | A dimmer switch is a switch that adjusts electrical power through a variable position level action.
|  |  |  | Dimmer Type | Text |  |  | A list of the available types of dimmer switch from which that required may be selected.
|  |  | Emergency Stop |  |  |  |  | An emergency stop device acts to remove as quickly as possible any danger that may have arisen unexpectedly.
|  |  |  | Switch Operation | Logic |  | True or False | Indicates operation of emergency stop switch.
|  |  | Keypad |  |  |  |  | A keypad is a switch supporting multiple functions.
|  |  |  | Keypad Type | Text |  |  | A list of the available types of keypad switch from which that required may be selected.
|  |  | Momentary |  |  |  |  | A momentary switch is a switch that does not hold state.
|  |  |  | Momentary Type | Text |  |  | A list of the available types of momentary switch from which that required may be selected.
|  |  |  | Set Point | Logic |  | 0,1 | Indicates the switch position over time
|  |  | Selector |  |  |  |  | A selector switch is a switch that adjusts electrical power through a multi-position action.
|  |  |  | Selector Type | Text |  |  | A list of the available types of selector switch from which that required may be selected.
|  |  |  | Switch Activation | Text |  |  | A list of the available activations for selector switches from which that required may be selected.
|  |  |  | Switch Usage | Text |  |  | A list of the available usages for selector switches from which that required may be selected.
|  |  | Starter |  |  |  |  | A starter is a switch which in the closed position controls the application of power to an electrical device.
|  |  |  | Starter Type | Text |  | AutoTransformer, Manual, DirectOnLine, Frequency, nStep, Rheostatic, StarDelta | A list of the available types of starter from which that required may be selected
|  |  | Disconnect |  |  |  |  | A switch disconnector is a switch which in the open position satisfies the isolating requirements specified for a disconnector.
|  |  |  | Load Disconnection Type | Text |  |  | A list of the available types of load disconnection from which that required may be selected.
|  |  |  | Switch Disconnector Type | Text |  | CenterBreak, DividedSupport, DoubleBreak, EarthingSwitch, Isolator | A list of the available types of switch disconnector from which that required may be selected
|  |  | Toggle |  |  |  |  | A toggle switch is a switch that enables or isolates electrical power through a two position on/off action.
|  |  |  | Switch Activation | Text |  |  | A list of the available activations for toggle switches from which that required may be selected.
|  |  |  | Switch Usage | Text |  |  | A list of the available usages for toggle switches from which that required may be selected.
|  |  |  | Toggle Switch Type | Text |  |  | A list of the available types of toggle switch from which that required may be selected.
|  | Transformer | [5 empty] | A transformer is an inductive stationary device that transfers electrical energy from one circuit to another.
|  |  | Imaginary Impedance Ratio |  | Numeric | Ratio |  | The ratio between the imaginary part of the zero sequence impedance and the imaginary part of the positive impedance (i.e. imaginary part of the short-circuit voltage) of the transformer. Used for three-phase transformer which includes a N-conductor. |  |  |  |  | x
|  |  | Is Neutral Primary Terminal Available |  | Logic |  | True or False | An indication of whether the neutral point of the primary winding is available as a terminal |  |  |  |  | x
|  |  | Is Neutral Secondary Terminal Available |  | Logic |  | True or False | An indication of whether the neutral point of the secondary winding is available as a terminal |  |  |  |  | x
|  |  | Maximum Apparent Power |  | Numeric | VA |  | Maximum apparent power/capacity in VA |  |  |  |  | x
|  |  | Primary Apparent Power |  | Numeric | VA |  | The power in VA that has been transformed and that runs into the transformer on the primary side. |  |  |  |  | x
|  |  | Primary Current |  | Numeric | Amps |  | The current that is going to be transformed and that runs into the transformer on the primary side. |  |  |  |  | x
|  |  | Primary Frequency |  | Numeric | Hertz |  | The frequency that is going to be transformed and that runs into the transformer on the primary side. |  |  |  |  | x
|  |  | Primary Voltage |  | Numeric | Volts |  | The voltage that is going to be transformed and that runs into the transformer on the primary side. |  |  |  |  | x
|  |  | Real Impedance Ratio |  | Numeric | Ratio |  | The ratio between the real part of the zero sequence impedance and the real part of the positive impedance (i.e. real part of the short-circuit voltage) of the transformer. Used for three-phase transformer which includes a N-conductor. |  |  |  |  | x
|  |  | Secondary Apparent Power |  | Numeric | VA |  | The power in VA (volt ampere) that has been transformed and is running out of the transformer on the secondary side. |  |  |  |  | x
|  |  | Secondary Current |  | Numeric | Amps |  | The current that has been transformed and is running out of the transformer on the secondary side. |  |  |  |  | x
|  |  | Secondary Current Type |  | Text |  |  | A list of the secondary current types that can result from transformer output. |  |  |  |  | x
|  |  | Secondary Frequency |  | Numeric | Hertz |  | The frequency that has been transformed and is running out of the transformer on the secondary side. |  |  |  |  | x
|  |  | Secondary Voltage |  | Numeric | Volts |  | The voltage that has been transformed and is running out of the transformer on the secondary side. |  |  |  |  | x
|  |  | Short Circuit Voltage |  | Numeric | Percentage |  | A complex number that specifies the real and imaginary parts of the short-circuit voltage at rated current of a transformer given in %. |  |  |  |  | x
|  |  | Transformer Vector Group |  | Text |  | D, Y, Z | List of the possible vector groups for the transformer from which that required may be set. D: means that the windings are delta-connected. Y: means that the windings are star-connected. Z: means that the windings are zig-zag connected (a special start-connected providing low reactance of the transformer); |  |  |  |  | x
Note on B12: Author: name change From Moel Label To : Product Name
Note on B13: Author: Changed Name From Model Reference To Model Designation

## D- Electrical Distribution
D- Electrical Distribution
Part 1 - Attribute Description | [8 empty] | Part 2 - LOD Profile |  |  |  |  | Part 3 - Example Project-Specific Milestones
[14 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
[5 empty] | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Global Attributes
None
Item-Specific Attributes
Cable Management
|  |  | Condition Status |  | Text |  | New, Existing, Demolish, Temporary, User Defined | Status of the element, predominately used in renovation or retrofitting projects |  |  |  |  | x
|  |  | ID Tag |  | Text |  |  | Reference ID for this specified type in this project (e.g. type 'A-1'), provided, if there is no classification reference to a recognized classification system used. |  |  | x | x | x
|  |  | Cable Ladder |  |  |  |  | An open carrier segment on which cables are carried on a ladder structure.
|  |  |  | Ladder Configuration | Text |  |  | Description of the configuration of the ladder structure used.
|  |  |  | Nominal Height | Numeric | Inches |  | The nominal height of the segment.
|  |  |  | Nominal Width | Numeric | Inches |  | The nominal width of the segment.
|  |  | Cable Tray |  |  |  |  | An (typically) open carrier segment onto which cables are laid.
|  |  |  | Has Cover | Logic |  | True or False | Indication of whether the cable tray has a cover (=TRUE) or not (= FALSE). By default, this value should be set to FALSE..
|  |  |  | Nominal Height | Numeric | Inches |  | The nominal height of the segment.
|  |  |  | Nominal Width | Numeric | Inches |  | The nominal width of the segment.
|  |  | Cable Trunk |  |  |  |  | An enclosed carrier segment with one or more compartments into which cables are placed.
|  |  |  | Nominal Height | Numeric | Inches |  | The nominal height of the segment.
|  |  |  | Nominal Width | Numeric | Inches |  | The nominal width of the segment.
|  |  |  | Number Of Compartments | Numeric |  |  | The number of separate internal compartments within the trunking.
|  |  | Conduit |  |  |  |  | An enclosed tubular carrier segment through which cables are pulled.
|  |  |  | Conduit Shape Type | Text |  |  | The shape of the conduit segment.
|  |  |  | Is Rigid | Logic |  | True or False | Indication of whether the conduit is rigid
|  |  |  | Nominal Height | Numeric | Inches |  | The nominal height of the segment.
|  |  |  | Nominal Width | Numeric | Inches |  | The nominal width of the segment.
Electrical Cable
|  |  | Carrier Stack Number |  | Numeric |  |  | Number of carrier segments (tray, ladder etc.) that are vertically stacked (vertical is measured as the z-axis of the local coordinate system of the carrier segment). |  |  |  | x | x
|  |  | Current Carrying Capacity |  | Numeric | Amps |  | Maximum value of electric current which can be carried continuously by a conductor, a device or an apparatu |  |  |  |  | x
|  |  | Design Ambient Temperature |  | Numeric | Degrees C |  | The highest and lowest local ambient temperature likely to be encountered. |  |  |  |  | x
|  |  | Distance Between Parallel Circuits |  | Numeric | Inches |  | Distance measured between parallel circuits. |  |  |  |  | x
|  |  | ID Tag |  | Text |  |  | Reference ID for this specified type in this project (e.g. type 'A-1'), provided, if there is no classification reference to a recognized classification system used. |  |  | x | x | x
|  |  | Installation Method |  | Text |  |  | Method of installation of cable/conductor. |  |  |  |  | x
|  |  | Installation Method Flag Enum |  | Text |  |  | Special installation conditions relating to particular types of installation based on IEC60364-5-52:2001 reference installation methods C and D. |  |  |  |  | x
|  |  | Is Horizontal Cable |  | Logic |  | True or False | Indication of whether the cable occurrences are mounted horizontally |  |  |  | x | x
|  |  | Is Mounted Flat Cable |  | Logic |  | True or False | Indication of whether the cable occurrences are mounted flat |  |  |  | x | x
|  |  | Maximum Cable Length |  | Numeric | Feet |  | Maximum cable length based on voltagedrop. |  |  |  |  | x
|  |  | Mounting Method |  | Text |  |  | The method of mounting cable segment on a cable carrier from which the method required can be selected. |  |  |  | x | x
|  |  | Number Of Parallel Circuits |  | Numeric |  |  | Number of parallel circuits. |  |  |  |  | x
|  |  | Power Loss |  | Numeric | Watts |  | Total loss of power across this cable. |  |  |  |  | x
|  |  | Soil Conductivity |  | Numeric | [SI] units of degK.m /W |  | Thermal conductivity of soil. Generally, within standards such as IEC 60364-5-52, table 52A-16 |  |  |  |  | x
|  |  | User Correction Factor |  | Numeric | Percentage |  | An arbitrary correction factor that may be applied by the user. |  |  |  |  | x
|  |  | Bus Bar |  |  |  |  | Properties specific to busbar cable segments.
|  |  |  | Busbar Routing | Logic |  | True or False | Indication of whether the busbar occurrences are routed horizontally
|  |  | Electrical Cable |  |  |  |  | Electrical cable with a specific purpose to lead electric current within a circuit or any other electric construction.
|  |  |  | Function Reliable | Logic |  | True or False | Cable/bus maintain given properties/functions over a given (tested) time and conditions. According to IEC standard.
|  |  |  | Halogen Proof | Logic |  | True or False | Produces small amount of smoke and irritating Deaerator/Gas.
|  |  |  | Has Protective Earth | Logic |  | True or False | One core has protective earth marked insulation, Yellow/Green.
|  |  |  | Maximum Operating Temperature | Numeric | Degrees C |  | The maximum temperature at which a cable or bus is certified to operate.
|  |  |  | Maximum Short Circuit Temperature | Numeric | Degrees C |  | The maximum short circuit temperature at which a cable or bus is certified to operate.
|  |  |  | Number Of Cores | Numeric |  |  | The number of cores in Cable/Bus.
|  |  |  | Overall Diameter | Numeric | Inches |  | The overall diameter of a Cable/Bus.
|  |  |  | Rated Temperature | Numeric | Degrees C |  | The range of allowed temerature that a device is certified to handle. The upper bound of this value is the maximum.
|  |  |  | Rated Voltage | Numeric | Volts |  | The range of allowed voltage that a device is certified to handle. The upper bound of this value is the maximum.
|  |  |  | Screen Diameter | Numeric | Inches |  | The diameter of the screen around a cable or bus segment (if present).
|  |  |  | Self Extinguishing60332_1 | Logic |  | True or False | Self Extinguishing cable/core according to IEC 60332.1.
|  |  |  | Self Extinguishing60332_3 | Logic |  | True or False | Self Extinguishing cable/core according to IEC 60332.3.
|  |  |  | Special Construction | Text |  |  | Special construction capabilities like self-supporting, flat devidable cable or bus flat non devidable cable or bus supporting elements inside
|  |  |  | Standard | Text |  |  | The designation of the standard applicable for the definition of the Cable/Bus used.
|  |  |  | Weight | Numeric | Lbs |  | Weight of cable kg/km.
|  |  | Electrical Conductor |  |  |  |  | An electrical conductor is a single linear element with the specific purpose to lead electric current.
|  |  |  | Construction | Text |  | Solid, Stranded | Purpose of informing on how the conductor is constucted (interwined or solid). I.e. Solid (IEV 461-01-06), stranded (IEV 461-01-07), solid-/finestranded(IEV 461-01-11) (not flexible/flexible).
|  |  |  | Cross Sectional Area | Numeric | Circular Mils (kcmil) |  | Cross section area of the phase(s) lead(s).
|  |  |  | Function | Text |  |  | Type of function for which the conductor is intended.
|  |  |  | Material | Text |  |  | Type of material from which the conductor is constructed.
|  |  |  | Shape | Text |  |  | Indication of the shape of the conductor.
|  |  | Insulated Conductor |  |  |  |  | An assembly comprising a conductor with its own insulation (and screens if any)
|  |  |  | Core Identifier | Text |  |  | The core identification used Identifiers may be used such as by color (Black, Brown, Grey) or by number (1, 2, 3) or by IEC phase reference (L1, L2, L3) etc.
|  |  |  | Function Reliable | Logic |  | True or False | Core maintain given properties/functions over a given (tested) time and conditions. According to (IEC) standard.
|  |  |  | Halogen Proof | Logic |  | True or False | Produces small amount of smoke and irritating deaerator/gas.
|  |  |  | Overall Diameter | Numeric | Inches |  | The overall diameter of a core (maximum space used).
|  |  |  | Rated Temperature | Numeric | C |  | The range of allowed temerature that a device is certified to handle. The upper bound of this value is the maximum.
|  |  |  | Rated Voltage | Numeric | Volts |  | The range of allowed voltage that a device is certified to handle. The upper bound of this value is the maximum.
|  |  |  | Screen Diameter | Numeric | Inches |  | The diameter of the screen around a core segment (if present).
|  |  |  | Self Extinguishing60332_1 | Logic |  | True or False | Self Extinguishing cable/core according to IEC 60332.1.
|  |  |  | Self Extinguishing60332_3 | Logic |  | True or False | Self Extinguishing cable/core according to IEC 60332.3.
|  |  |  | Sheath Colors | Text |  |  | Colour of the core (derived from IEC 60757).
|  |  |  | Standard | Text |  |  | The designation of the standard applicable for the definition of the core used.
|  |  |  | Weight | Numeric | Lbs |  | Weight of core kg/km.
|  |  |  | Power State | Logic |  | 0,1 | Indicates the power state of the device where True is on and False is off.
Electrical Properties
|  |  |  | Conductor Function | Text |  |  | Function of a line conductor to which a device is intended to be connected where L1, L2 and L3 represent the phase lines according to IEC 60446 notation
|  |  |  | Has Protective Earth | Logic |  | True or False | Indicates whether the electrical device has a protective earth connection
|  |  |  | Insulation Standard Class | Text |  |  | Insulation standard classes provides basic protection information against electric shock. Defines levels of insulation required in terms of constructional requirements
|  |  |  | I P_ Code | Text |  |  | IEC 60529 Classification of degrees of protection provided by enclosures (IP Code).
|  |  |  | Nominal Frequency Range | Numeric | Hertz |  | The upper and lower limits of frequency for which the operation of the device is certified.
|  |  |  | Number Of Poles | Numeric |  |  | The number of live lines that is intended to be handled by the device.
|  |  |  | Power Factor | Numeric | Ratio |  | The ratio between the rated electrical power and the product of the rated current and rated voltage
|  |  |  | Rated Current | Numeric | Amps |  | The current that a device is designed to handle.
|  |  |  | Rated Voltage | Numeric | Volts |  | The voltage that a device is designed to handle.

## Appendix- B Bridge Steel
Appendix- B Bridge Steel
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
AISC Shape Type & Size | String | Text | options: [specific “HSS 6x6x1/4”] |  |  |  | x | x | x
Fireproofed | bool | True / False |  |  |  |  | x | x | x
Weight in pounds/foot | Decimal
ASTM Material Grade | String | Text | options: [A992, etc] |  |  |  |  | x | x
Coating | String | Text | options: [galvanized, painted for exterior exposure, etc]
Archtectural Exposed Structural Steel | bool | True / False | options: [yes, no]
Fabrication Sequence Number | Interger | Number |  | SequenceNumber |  |  |  | x | x
Shop Submital Parameters |  |  |  | {}
Date - Issued For Construction | Date Time |  |  | {DateIFC}
Date - Permited | Date Time |  |  | {DatePermitted}
Date - recieved for Shop Detailing | Date Time |  |  | {DateRecievedForShopDet}
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | {DateOutForAproval}
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | {DateFinalForFab}
Date - Fabrication Start | Date Time |  |  | {DateFabStart}
Date - Fabrication End | Date Time |  |  | {DateFabEnd}
Date - Fabrication Shipped | Date Time |  |  | {DateFabShip}
Date - Fabrication Received | Date Time |  |  | {DateFabRecieved}
Date - Erection | Date Time |  |  | {DateErected}
Date - Inspected | Date Time |  |  | {DateInspected}

## Appendix- B Bridge Concrete
Appendix- B Bridge Concrete
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Member Type | Integer |  | (0) Foundation (1) Beam (2) Column (3) Slab (4) Wall |  |  | x | x | x | x
Concrete Compression Strength |  | PSI |  | Example: 3000 PSI |  |  | x | x | x
Reinforcing Steel Flexture |  | PSI |  | Example: 60,000 PSI |  |  | x | x | x
Reinforcing Steel Shear |  | PSI |  | Example: 60,000 PSI |  |  | x | x | x
Member Casting Number
Exterior Exposure | Bool | True \ False
Shop Submital Parameters
Date - Issued For Construction | Date Time |  |  | DateIFC
Date - Permited | Date Time |  |  | DatePermitted
Date - recieved for Shop Detailing | Date Time |  |  | DateRecievedForShopDet
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | DateOutForAproval
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | DateFinalForFab
Date - Fabrication Start | Date Time |  |  | DateFabStart
Date - Fabrication End | Date Time |  |  | DateFabEnd
Date - Fabrication Shipped | Date Time |  |  | DateFabShip
Date - Fabrication Received | Date Time |  |  | DateFabRecieved
Date - Erection | Date Time |  |  | DateErected
Date - Inspected | Date Time |  |  | DateInspected

## Appendix- B Bridge Precast
Appendix- B Bridge Precast
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
Member Type | Integer |  | (0) Foundation (1) Beam (2) Column (3) Slab (4) Wall |  |  | x | x | x | x
Concrete Compression Strength |  | PSI |  | Example: 3000 PSI |  |  | x | x | x
Reinforcing Steel Flexture |  | PSI |  | Example: 60,000 PSI |  |  | x | x | x
Reinforcing Steel Shear |  | PSI |  | Example: 60,000 PSI |  |  | x | x | x
Member Casting Number
Exterior Exposure | Bool | True \ False
Shop Submital Parameters
Date - Issued For Construction | Date Time |  |  | DateIFC
Date - Permited | Date Time |  |  | DatePermitted
Date - recieved for Shop Detailing | Date Time |  |  | DateRecievedForShopDet
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | DateOutForAproval
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | DateFinalForFab
Date - Fabrication Start | Date Time |  |  | DateFabStart
Date - Fabrication End | Date Time |  |  | DateFabEnd
Date - Fabrication Shipped | Date Time |  |  | DateFabShip
Date - Fabrication Received | Date Time |  |  | DateFabRecieved
Date - Erection | Date Time |  |  | DateErected
Date - Inspected | Date Time |  |  | DateInspected

## Appendix- F Metal Buildings
Appendix- F Metal Buildings
Part 1 - Attribute Description |  |  |  |  | Part 2 - LOD Profile |  |  |  |  | Part 3 - Project-Specific Milestones (Examples)
[10 empty] | Estimating | Estimating | LEED Cert. | LEED Cert
Attribute | Data Type | Units | Option Examples | Commentary | 100 | 200 | 300 | 350 | 400 | Est. 1 | Bid Pkg. | Check | Submittal
AISC Shape Type & Size | String | Text | options: [specific “HSS 6x6x1/4”] |  |  |  | x | x | x
Fireproofed | bool | True / False |  |  |  |  | x | x | x
Weight in pounds/foot | Decimal
ASTM Material Grade | String | Text | options: [A992, etc] |  |  |  |  | x | x
Coating | String | Text | options: [galvanized, painted for exterior exposure, etc]
Archtectural Exposed Structural Steel | bool | True / False | options: [yes, no]
Fabrication Sequence Number | Interger | Number |  | SequenceNumber |  |  |  | x | x
Shop Submital Parameters |  |  |  | {}
Date - Issued For Construction | Date Time |  |  | {DateIFC}
Date - Permited | Date Time |  |  | {DatePermitted}
Date - recieved for Shop Detailing | Date Time |  |  | {DateRecievedForShopDet}
Date - Detailing Submited for EOR review \ Out For Aproval (OFA) | Date Time |  |  | {DateOutForAproval}
Date - Final Erection Drawings Aproved for Fab | Date Time |  |  | {DateFinalForFab}
Date - Fabrication Start | Date Time |  |  | {DateFabStart}
Date - Fabrication End | Date Time |  |  | {DateFabEnd}
Date - Fabrication Shipped | Date Time |  |  | {DateFabShip}
Date - Fabrication Received | Date Time |  |  | {DateFabRecieved}
Date - Erection | Date Time |  |  | {DateErected}
Date - Inspected | Date Time |  |  | {DateInspected}